# GENERAL

## The requirements of the Contract, Division [1] [01], and Division [16] [26] apply to work in this Section.

## SECTION INCLUDES

### Medium Voltage, 27KV and 38KV, Metal-Clad Switchgear.

## RELATED SECTIONS

### Section [16140 – Power Equipment Centers] [13 34 23.23 – Fabricated Substation Control Room]

## REFERENCES

## The medium voltage metal-clad switchgear and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/IEEE C37.20.2, Metal-Clad Switchgear.

### ANSI/IEEE C37.04, Rating Structure for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis.

### ANSI/IEEE C37.06, Switchgear - AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis - Preferred Ratings and Related Required Capabilities.

### ANSI/IEEE C37.09, Test Procedures for AC High-Voltage Circuit Breakers.

### ANSI/IEEE C37.010, Application Guide for AC High-Voltage Circuit Breakers.

### ANSI/IEEE C37.11, AC High-Voltage Circuit Breaker Control Requirements.

### ANSI/IEEE C37.90, Standard for Relays and Relay Systems Associated with Electric Power Apparatus.

### ANSI/IEEE C37.100, Definitions for Power Switchgear.

### NEMA SG 2, High-Voltage Fuses.

### NEMA SG 4, Alternating - Current High-Voltage Circuit Breaker.

### NEMA SG 5, Power Switchgear Assemblies.

## DEFINITIONS

## SYSTEM DESCRIPTION

### [Indoor] [Outdoor] [protected aisle] [common aisle] [equipment center] metal-clad switchgear intended for use on [xx.x] KV, 3-phase,  [3] [4] wire [grounded] [ungrounded] [Impedance grounded] 60-Hz system.  Switchgear shall be rated as indicated on drawings and have removable-element vacuum circuit breakers. Entire lineup and circuit breaker(s), as a unit, shall have a Basic Impulse Level rating of [125] [150] [200] KV.

### Equipment shall be completely factory-built, assembled, wired, and tested.  All equipment and components shall be of new construction.

## SUBMITTALS

### Manufacturer shall provide copies of following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26]:

#### Product Data on a specified product.

#### Shop Drawings on a specified product.

#### Certified copies of all Type (Design) and Verification Test Reports on a specified product.

## PROJECT RECORD DOCUMENTS

### Maintain an up-to-date set of Contract documents.  Note any and all revisions and deviations that are made during the course of the project.

## OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide copies of installation, operation and maintenance procedures to purchaser in accordance with general requirements of Division [1] [01] and Division [16] [26].

### Submit operation and maintenance data based on factory and field testing, operation and maintenance of specified product.

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of medium voltage metal-clad switchgear for a minimum of [20] years.

### Manufacturer's Certificate of ISO 9001 or 9002 Compliance.

## REGULATORY REQUIREMENTS

## DELIVERY, STORAGE, AND HANDLING

### Deliver, store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Deliver in maximum two section shipping splits, for ease of handling, unless otherwise specified.  Each shipping split section shall be mounted on shipping skids and wrapped for protection.  If switchgear equipment will be shipped to an equipment center fabricator at a separate location, the switchgear manufacturer will coordinate shipping and installation of the equipment within the powerhouse.

### Inspect and report concealed damage to carrier within [specified time].

### Store in a clean, dry space.  Maintain factory protection or cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic. Customer to supply 120VAC control power to energize space heaters within equipment, to prevent condensation.

### Handle in accordance with manufacturer's written instructions to avoid damaging equipment, installed devices, and finish.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after switchgear installation.

### Switchgear shall be located in well-ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus [30] and plus [40] degrees C. Indoor locations shall be protected to prevent moisture from entering enclosure.

## SEQUENCING AND SCHEDULING

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 12 months from date of installation or 18 months from date of shipment, whichever occurs first.

## EXTRA MATERIALS

### Provide all spare parts that manufacturer recommends for startup.

### Provide list of spare parts which manufacturer recommends for purchase by customer for first two years of equipment operation.

## FIELD MEASUREMENTS

### Make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in local codes and standards.

# PRODUCTS

## MANUFACTURER

### Manufacturer shall be GE or approved equal listed below:

### Cutler-Hammer

### Siemens

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions.  Manufacturers listed above are not relieved from meeting these specifications in their entirety.  Products in compliance with the specification and manufactured by others not named will not be considered unless pre-approved by the engineer of record ten(10) days prior to bid date.

## EQUIPMENT

### GE Medium Voltage Metal-Clad Switchgear has been used for the basis of design, as indicated on the contract design drawings.

## COMPONENTS

### Refer to Drawings for: actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; and other required details.

### Enclosure

#### Switchgear shall consist of breaker and auxiliary units, as indicated in drawings, assembled to form a rigid, self-supporting, structure.  Outdoor metal-clad switchgear shall be enclosed in a weatherproof equipment center (powerhouse) and shall include suitable weatherproof access doors, doors with provision for padlocking; protected ventilation openings as required; interior lighting, utility outlets with protective devices; and equipment heaters with protective devices.  In each unit, major primary circuit parts (breaker, buses, transformers) shall be completely enclosed by grounded metal barriers, including a front barrier as part of the circuit breaker.  See Specification [16140] [13 34 23.23] for equipment center details/requirements.

#### Switchgear sections shall be arranged similar to as shown on attached drawings.

#### Switchgear will be a complete self-supporting structure of the required number of vertical sections bolted together to form one single line-up. Vertical section barriers, rear covers, and roofs will be 11-gauge steel.  Equipment shall be provided with lifting facilities.

#### All bus joints, taps, splices and outgoing connections shall be insulated.  The manufacturer shall provide bolt torque instructions.

#### Each cubicle that has high voltage connections shall be effectively isolated from the others and from low voltage sections by 11-gauge metal barriers.  All high voltage connections in these compartments shall be accessible through removable cover plates or doors.  The voltage and current transformer secondary wiring runs in high voltage compartments shall be shielded or routed in metal conduit.  Removable cover plates shall be provided for access to buses, voltage and current transformers, low voltage wires, etc.  The relay panels or doors shall be isolated from the high voltage connections by grounded metal panels.

#### All doors shall be hinged with formed welded edges and provided, as required, with doorstops and louvers.  For outdoor applications, doors with louvers shall include 1/8" mesh aluminum backup vermin screens.  Doors shall have a minimum of 105° opening and be so designed that there will be no interference with devices when the circuit breakers are inserted or removed.

#### Provision shall be made in the appropriate switchgear cubicles for the entrance of conduits containing the low voltage control and auxiliary power cables, and necessary connections to interposing relays, auxiliary transformers, and voltage regulating equipment, and other low voltage wiring.  In outdoor cubicles, a floor plate shall be supplied with provision for the entrance of the cables and/or conduits.

#### The cable compartment shall be located at the rear of the structure and shall provide adequate facilities for terminating cables.  At least 36-inches of vertical space shall be provided to accommodate cable bending radius and stress cone terminations.  For outdoor applications, the rear compartment access doors shall be hinged and latched and shall have provisions for padlocking.  Doorstops and stop catches shall also be furnished.

#### Incoming cables will be [top][bottom] entry.  Terminal connectors for cable connections will use NEMA 2-hole drilling and pad adapters where required (for multiple cables) and be silver-plated copper.

#### Each circuit breaker [27][38] KV shall be mounted in a steel framework cell equipped with a guide rail mechanism and self-coupling, self-aligning primary and secondary disconnecting devices (contacts).  Circuit breakers requiring manual engagement of secondary disconnects, or that require the use of umbilical cords or manual plug and socket connection of secondary disconnects are not permitted.  All breakers of the same type and rating, listed in the detail specification must be entirely interchangeable with each other.  Breakers shall be roll-out, and located in the bottom cubicle only.

#### Interlocks to prevent racking breaker into or from connected position with breaker closed must be included.  A positive stop will prevent over-travel when in the connected position.  The design of the mechanism will be such that the removable breaker will be self-aligning and will be held rigidly in the connected position without the necessity of locking bars or bolts.  Contact wear indicators shall be provided.

#### Automatic grounded metal safety shutters will close the entrance to the stationary primary disconnecting devices when the breaker is in the test or withdrawn position.

#### All main bus supports shall be of high-strength electrical grade wet process porcelain or clycloapliphatic epoxy.

#### This equipment shall be shipped assembled to the maximum possible extent.

#### The primary disconnecting contacts shall be constructed of silver-plated copper.  All moveable contact fingers and springs shall be mounted on the circuit breaker where they may be easily inspected.

##### The breaker is automatically tripped when moving the circuit breaker to the connected position before the primary shutters open.

##### The breaker is trip-free mechanically and electrically during racking.

##### The breaker can be racked in with the door open or closed.

##### The breaker closing spring is automatically discharged as the breaker is withdrawn from the cell.

##### A latch secures the breaker in the connected, disconnected, or test position with the door open or closed.

##### The circuit breaker is grounded throughout its' travel through all positions (first make - last break).

##### Positive indication of the breaker position shall be provided for connected, test, and disconnected positions.

#### Manufacturer shall furnish all necessary power and control interconnections between cubicles.

#### All of the control cables shall enter as shown on the drawings.

#### Cable troughs for wiring between the circuit breaker cubicles and the miscellaneous cubicles shall be located internal to the Switchgear.

#### Furnish nameplates for each device as indicated in drawings. Nameplates shall be black letters on white background.  Nameplates shall be fastened by aluminum rivets, or stainless steel screws.  There shall be a master nameplate that indicates equipment ratings, manufacturer's name, shop order number and information as required by ANSI C37.20.2.

### Main Bus

#### The main bus shall be electrical grade copper [1200A][2000A][3000A] and rated as indicated on drawings.  Bus bars shall have a continuous current rating as limited by ANSI standards to temperature rise and documented by design tests.  All joints will be silver plated,[tin plating option] with at least 2 bolts per joint, using zinc plated hardware.  Where high currents are encountered, which may create excessive joint heat, stainless steel hardware shall be used.

#### Bus bars will be braced to withstand magnetic stresses developed by currents equal to main power circuit breaker close, carry, and interrupting ratings.  Access to bus bars shall be through removable front panels.

#### Bus bars shall be covered with Lexan sleeving, and Lexan boots shall be used for insulating bus and joints.  Taping of bus systems is not permitted.

#### All bus connections will be rated to carry the full frame size continuous current rating of the associated breaker; tapered bus is not allowed.

### Ground Bus

#### A full length [bare][silver-plated][tin-plated] copper ground bus (1/4 by 2 inch cross-section) shall be provided at the bottom of the lineup.  It will be connected to each breaker grounding contact, and drilled to accept a 2-hole lug used to terminate the incoming/outgoing equipment ground conductor(s).

#### The bus shall also be drilled to accommodate a ground lug on the first and last section of the lineup; to facilitate connections to the ground grid.

#### Extension provisions similar to those of the power buses shall be provided.

### Circuit Breakers

#### All of the circuit breakers shall be [27][38] kV class, 3-pole, single throw, automatic and electrically and mechanically trip free with a [16][25][31.5][40] KA interrupting rating at K= 1.0.  Each circuit breaker position shall be equipped with one 4-stage set of auxiliary switches in addition to the auxiliary switches required for normal circuit breaker control and operation.  The circuit breaker element shall be stored energy type,           V[DC][AC] close and            V [DC][AC] trip.

#### Protective front covers shall be provided on the circuit breaker element to prevent access to the operating mechanism or live parts when the circuit breaker is in the connected position.

#### All circuit breakers shall be vacuum interrupter, horizontal draw-out type, provided with self-aligning, line-side and load-side disconnecting devices.  Each breaker shall be provided with a motor-charged spring, stored energy operating mechanism.  The stored energy mechanism shall be charged normally by a universal electric motor and in emergency situations, by a manual handle.

#### The primary disconnecting fingers shall be silver-plated and retained to the primary contacts with individual leaf springs.  The secondary disconnecting contact shall be a plated, multiple contact, plug.  The plugs shall automatically engage the housing sockets in the breaker operating positions.  The use of manual plug and socket secondary disconnecting devices are not permitted.

#### Circuit breakers of the same ratings and control voltage shall be completely interchangeable.

#### The breaker front panel shall be a grounded steel barrier that effectively isolates the instrument and control compartments.  The front panel shall have the following control and indication features.

##### Breaker open-close indication.

##### Closing springs charged-discharged indication.

##### Operations counter.

##### Manual trip-close push buttons.

#### Switchgear shutters shall be permanently marked to indicate the "Bus" or "Feeder" side primary stationary disconnects.  Phase markings shall also be included.

#### The circuit breaker shall be mechanically interlocked as follows:

##### It shall not be possible to insert or remove a circuit breaker element from the connected position while the interrupters are in the closed position.  The stored energy mechanism shall be discharged automatically prior to the circuit breaker element being withdrawn from, or inserted into, the cubicle.

#### Manual operating devices for racking the circuit breaker elements in and out of their cubicle shall be provided.

#### An extension jumper shall be provided for each switchgear assembly so that the circuit breaker, and the circuit breaker's operation, may be checked with the element outside of the circuit breaker cubicle.

### Instrument Transformers

#### Current transformers shall be dry type, and rated as indicated on the drawings.  They shall have sufficient thermal and mechanical capacity to withstand the maximum momentary current rating of the breakers.  The secondary terminals shall be of the solder-less clamp type.  All current transformers shall be properly identified for polarity with standard marking symbols.  The minimum acceptable accuracy class for metering and relaying shall be in accordance with the latest edition of ANSI Standard C37.20.  Window type CT's having an insulation rating of 600V, and having fully insulated bus centered in the transformer window opening, shall be acceptable when ionization and impulse tests prove a satisfactory arrangement.  Phase CT's shall be mounted over stationary primary disconnects.  Ground sensor CT’s shall be mounted within the cable compartment and sized to accept quantity/size of power cables indicated on the single-line diagram.  All CT leads shall be wired via shorting terminal blocks.

#### Each set of voltage transformers (PT’s) and their primary fuses shall be mounted in separate steel compartments.  Primary connections to the transformers shall be insulated and enter the compartment through porcelain bushings.  Each set of voltage transformers and fuses shall be mounted on the draw-out steel carriage which will be capable of disconnecting the transformer fuses from their voltage source and removing them from the structure.  This removing mechanism shall be so arranged that full access to the transformers cannot be accomplished until the fuses are disconnected from the structure. When moved to a full out position, the transformer fuses and PT windings shall be automatically connected to equipment ground.  Primary contacts shall be insulated from the structure by porcelain supports and shall be self-aligning and have silver to silver contact surfaces.

#### Control Power Transformers (CPT’s) rated above 15KVA shall be stationary mounted.  Fuses shall be draw-out and mechanically interlocked with a secondary breaker to prevent draw-out with secondary breaker closed.  CPT shall be sized by switchgear manufacturer.

### CONTROL AND AUXILIARY SWITCHES/LIGHTS

#### Control switches shall be rotary, multi-position, cam-operated, multi-stage type with dust cover and silver-to-silver contacts rated 600 volt and 20 amperes.  Breaker control switches and selector switches shall have "pistol grip" handles.  Meter switches shall all have "knurled knob" handles.  Lockout switches shall have "oval" handles.

#### Each circuit breaker unit shall be provided with a breaker control switch and two indicating lights, red (breaker closed) green (breaker open).  Control switches shall be three-position (close-off-trip) with spring return to center.  Pistol grip handles to be provided.

#### Each incoming line main circuit breaker, bus tie circuit breaker, and feeder circuit breaker unit shall be provided with a Truck Operated Cell (TOC) auxiliary switch.  The TOC switch shall operate when the circuit breaker is racked into the connected position only.  The Mechanism Operated Contact (MOC) auxiliary switch shall operate when the breaker closes and in either the connected or test positions.  The TOC switch shall have a minimum of two normally open and two normally closed contacts rated at 10 amperes and 125 VDC.  The MOC auxiliary switch shall have a minimum of five normally open and five normally closed contacts rated 10 amperes. All auxiliary switches shall be wired to terminal blocks located in the breaker compartment.

#### Indicating lights shall be of the series resistor type with color caps designed for maximum visibility, low wattage consumption of the lamps (maximum 2 watts) and long service life shall be provided.  Green and red indicating lights shall show the open and closed positions of the circuit breaker.  Light Emitting Diode (LED) lights may be substituted.

### UTILITY METERING (IF REQUIRED)

#### Where shown on drawings, provide separate barriered-off utility metering compartment or structure complete with hinged sealable door.  Bus work shall include provisions for mounting utility company current transformers and potential transformers as required by the utility company.  Drawing of utility company metering stack complete with dimensions and spacing requirements, shall be furnished to switchgear manufacturer.

### WIRING

#### Each switchgear line up shall be completely assembled, wired, and tested at the factory, including all buses, connections, insulators, terminals, and terminal blocks.

#### Secondary wiring shall be firmly laced and secured and terminated in approved molded-type terminal blocks conveniently located with respect to shipping splits and control conduit terminals.

#### Terminal blocks shall have approved covers and shall be mounted such that the wires to them can be grouped and laced together in a neat and workable manner.  A sufficient number of terminal connections including 15 percent of spare terminals shall be provided for all control and instrument wiring.

#### All secondary wiring shall be No. 14 AWG or larger, 90°C, 600 volt switchboard wire, type SIS, stranded, tinned copper and provided with PVC sleeve type wire markers on both ends.

#### All current transformers and associated circuitry control wiring shall be terminated with insulated ring-tongue or locking spade terminals.

#### Terminal blocks shall be GE type EB, with appropriate EB or equal shorting blocks provided for current transformers.

#### Two-pole, pullout disconnecting fuse blocks (with fuses) to be provided for each breaker to protect trip and close circuits.

### HEATERS

#### Each vertical section shall be provided with tubular type space heaters, with protective shields.  The heaters shall be rated a 240VAC and operated at 120VAC for long life.

#### The heaters shall be wired out for connection to temporary power during equipment storage at the jobsite, during construction.

## PROTECTIVE DEVICES

## NOTE TO SPECIFIER: Specifier to paste in relaying specification sections for specific relays including power monitoring communications if applicable for use in the switchgear equipment.

### Protective Devices - Protective relays shall be GE/MULTILIN relays or other approved relays as indicated below:

## NOTE TO SPECIFER:  Specifier to paste in  metering specification sections for specific meters including power monitoring communications if applicable for use in the switchgear equipment.

## METERING DEVICES

### Metering - Meters/monitors shall be GE EPM series or GE / MULTILIN meters or other approved equivalent devices as indicated below:

## ACCESSORIES

### Manual racking handle.

### Special tools needed for routine maintenance.

### Control jumper for checking breakers outside the stationary structures.

### One tube of contact lubricant.

### One container touch-up paint.

### One complete spare Circuit Breaker element (Option).

## FINISH

### All steel surfaces shall be chemically cleaned and treated to provide a bond between primer and metal surfaces to prevent the entrance of moisture and the formation of rust under the paint.  Exterior finish shall consist of a 0.75 – 1.0 mils of primer, and two top coats of finish paint.  The overall finish shall be minimum 3 mils in thickness.

### Color shall be ANSI 61 gray unless otherwise noted.

## TESTING

### The switchgear equipment and circuit breakers shall receive factory production tests per ANSI C37.20.2-1999 paragraph 6.3 and additional factory tests required by the manufacturer’s quality control department.  This should ensure the product will maintain a high quality standard of materials and reliability in operation.  The following tests shall be performed on each breaker element:

##### Alignment test with master cell to verify all interfaces and interchangeability.

##### Circuit breakers operated over the range of minimum to maximum control voltage.

##### Factory setting of contact gap.

##### Dielectric test.

### The following tests shall be performed on each breaker housing:

##### Alignment test with master breaker to verify interfaces.

##### Dielectric tests on primary and secondary circuits.

##### Operation of wiring, relays and other devices verified by an operational sequence test .

### Manufacturer shall provide three(3) copies of certified test reports verifying completion of factory production tests.

### Factory tests as outlined in section 2.08(B) shall be witnessed by the owner’s representative.  The manufacturer shall notify the owner two(2) weeks prior to the date the tests are to be performed.

# EXECUTION

## EXAMINATION

### Examine installation area to assure there is enough clearance to install switchgear.

### Check concrete pads for uniformity and level surface.

### Verify that medium voltage metal-clad switchgear are ready to install.

### Verify field measurements are as shown on drawings.

### Verify that required utilities are available, in proper location and ready for use.

### Beginning of installation means installer accepts conditions.

## LOCATION

## INSTALLATION

## Additional provisions and editing may be required for this part.

### Installer's Certificate of ISO 9000 Compliance.

### Installer has specialized in installing medium voltage metal-clad switchgear with minimum 10 years documented experience.

### Install per manufacturer's instructions.

### Install required safety labels.

## FIELD QUALITY CONTROL

### Inspect installed switchgear for anchoring, alignment, grounding and physical damage.

### Check tightness of all accessible electrical connections with a calibrated torque wrench. Minimum acceptable values are specified in manufacturer's instructions.

### Megger and record phase to phase and phase to ground insulation resistance of each bus section. Megger for [1] minute(s) for each measurement at minimum voltage of [1000] VDC. Measured Insulation resistance shall be at least [1] megohm(s).

### Test each key interlock system for proper functioning.

### Provide the services of a qualified factory-trained manufacturer’s representative to assist the contractor in installation and startup of the equipment specified under this section for a period of five(5) working days.  The manufacturer’s representative shall provide technical direction and assistance to the contractor in general assembly of the equipment , connections and adjustments, and testing of the assembly and components contained therein.

## ADJUSTING

### Adjust all circuit breakers, switches, access doors, operating handles for free mechanical and / or electrical operation as described in manufacturer's instructions.

### Return "odd" Kirk keys to Owner before energizing equipment.

### The relays shall be programmed (set) in the field by a qualified representative of the manufacturer, retained by the Contractor, in accordance with settings designated in the coordination study of the system as required elsewhere in the contract documents.

## CLEANING

### Wipe-down clean and vacuum interiors of equipment to remove construction debris, dirt, and  shipping materials.

### Repaint scratched or marred exterior surfaces to match original finish.

## END OF SECTION