# GENERAL

## SCOPE

### The (Contractor) (Owner) shall furnish, where indicated, a free-standing, (front access) dead front type low-voltage distribution switchboard, utilizing group mounted circuit protective devices, integrated panelboards, integrated dry-type transformers, and other equipment as specified herein, and as shown on the contract drawings

## RELATED SECTIONS

### [16465] [26 22 13] Low Voltage Dry Type Transformers

### [16471] [26 24 16 02] Power Distribution Panels.doc

### [16470] [26 24 16 01] Lighting Panelboards

## REFERENCES

### The low voltage distribution switchboards and all components shall be designed, manufactured and tested in accordance with the latest applicable following standards:

#### NEMA PB1

#### UL Standard 891

#### UL 67

#### UL 50

#### UL 489

#### NEMA ST20

#### UL 508

## SUBMITTALS – FOR REVIEW / APPROVAL

### Manufacturer shall provide three (3) copies of the following documents to (Owner) (Engineer) for review:

#### Front View Elevation

#### Master Drawing Index

#### Single Line

#### Schematic Diagram

#### Nameplate Schedule

#### Conduit Entry/Exit Locations

#### Major Component Ratings Including

##### Voltage

##### Continuous Current

##### Interrupting Ratings

#### Assembly Ratings Including

##### Voltage

##### Continuous Ratings

##### Interrupting Ratings

## SUBMITTALS – FOR CONSTRUCTION

### The following information shall be submitted:

#### Final As Built Drawings.  The final (as built) drawings shall include the same drawings as the original construction drawings and shall incorporate all changes made during the manufacturing process

#### Installation Instructions

## QUALIFICATIONS

### The manufacturer of the assembly shall be the manufacturer of the circuit protective devices within the assembly

### The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of five (5) years.  When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

## REGULATORY REQUIREMENTS

### The low voltage switchboard shall be UL labeled.

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall store, protect, and handle products in accordance with recommended practices listed in manufacturer’s Installation and Maintenance Manuals.

### Contractor shall inspect and report concealed damage to carrier within 48 hours.

### Contractor shall store in a clean, dry space.  Cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic.  Heat enclosures to prevent condensation.

### Contactor shall handle in accordance with manufacturer’s recommendations to avoid damaging equipment, installed devices, and finish.

## OPERATING AND MAINTENANCE MANUALS

### Equipment operating and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins, and renewal parts lists where applicable, for the complete assembly of each major component.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for one year (12 months) from date of installation of eighteen (18) months from date of purchase, whichever occurs first.

# PRODUCTS

## MANUFACTURERS

### General Electric or approved equal

### General Electric Company products have been used as the basis for design.  Other manufacturer’s products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer’s discretion, if they comply with all requirements (including UL and NEMA) specified or indicated in these Contract documents.

## RATINGS

### The assembly shall be rated to withstand mechanical forces exerted during short circuit conditions when connected directly to a power source having available fault current of  [10,000] [65,000] [100,000] amperes symmetrical (at rated voltage) (as shown on drawings).

### Short circuit rating shall be the interrupting rating of lowest rated device in the panel or applicable UL series rating of proper main and branch device combinations.

### Series combinations are required to be tested by UL and values predicted by the use of let through curves are not acceptable.  Switchboards that are series rated to short circuit requirements shall be appropriately labeled.

### Switchboard protective devices shall be furnished as listed on drawings and specified herein, including interconnections, instrumentation and control wiring.  Switchboards and devices shall be rated for the voltage and frequency listed on the drawings.

### Switchboard service entrance sections shall comply with UL service entrance requirements including a UL service entrance label, incoming line isolation barriers, and a removable neutral bond to switchboard ground for solidly grounded wye systems.

## CONSTRUCTION

### Switchboard shall consist of the required number of vertical sections bolted together to form a rigid assembly.  The sides and rear shall be covered with removable bolt on covers.  All edges of front covers or hinged front panels shall be formed.  Provide adequate ventilation within the enclosure

### Switchboards shall be fully self-supporting structures with ninety (90) inch tall vertical sections (excluding lifting eyes and pull boxes) bolted together to form the required arrangement.

### Switchboard shall be NEMA 1 dead front construction

### All sections of the switchboard shall be rear aligned with depth as shown on the drawings.  All protective devices shall be group mounted.  Devices shall be front removable and load connections front accessible enabling switchboard to be mounted against a wall.

### The assembly shall be provided with adequate lifting means.

### Switchboard to be provided with barriers between each vertical section.

## BUS

### All bus bars shall be [silver plated copper] [silver plated aluminum].  Main horizontal bus bars shall be mounted with all three phases arranged in the same vertical plane.  Bus sizing shall be based on NEMA standard temperature rise criteria of 65 degrees C over a 40 degrees C ambient [outside the enclosure].  Bus shall be braced for [65,000 AIC] [100,000 AIC].

### Provide a full capacity neutral bus where a neutral bus is indicated on the drawings.

### A copper ground bus (minimum ¼ x 2 inch), shall be furnished firmly secured to each vertical section structure and shall extend the entire length of the switchboard.

### All hardware used on conductors shall be high tensile strength and zinc plated.  All bus joints shall be provided with conical spring type washers.  Bellville washers used only on aluminum connections.

## WIRING / TERMINATIONS

### Small wiring, necessary fuse blocks, and terminal blocks within the switchboard shall be furnished as required.  Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, etc., shall be suitably marked for identification corresponding to appropriated designations on manufacturer’s wiring diagrams.

### Mechanical type terminals shall be provided for all line and load terminations suitable for copper of aluminum cable rated for 75 degrees C of the size as indicated on the drawings.

### Lugs shall be provided in the incoming line section for connection of the main grounding conductor.  Additional lugs for connection of other grounding conductors shall be provided as indicated on the drawings.

### All control wire shall be type SIS, bundled and secured with nylon ties.  Insulated locking spade terminals shall be provided for all control connections, except where saddle type terminals are provided integral to a device.  All current transformer secondary leads shall first be connected to conveniently accessible short circuit terminal blocks before connecting to any other device.  All groups of control wires leaving the switchboard shall be provided with terminal blocks with suitable numbering strips.  Provide wire markers at each end of all control wiring.

### The switchboard manufacturer shall wire all panelboards from the associated feeder breaker to the panelboard as noted on the drawings.  The wiring to be installed in the factory and shall not be installed in the field.

## INTEGRATED PANELBOARDS

### The switchboard manufacturer as shown on the contract drawings shall integrate and assemble panelboards into the switchboard.  The panel shall be recessed in the switchboard enclosure a minimum of four inches from the front of the switchboard to allow easy access to line and/or load conductors entering/exiting bottom.  Three quarter inch (3/4) breakers shall not be used in any part of the panelboard.

### Integrated panelboards shall be General Electric type.  Ratings of the panelboards shall meet marked ratings of the switchboard.

### Integrated panelboards to have standard door configurations.

### Integrated panelboards shall meet other criteria as shown in Section 16160.

## INTEGRATED DRY TYPE TRANSFORMERS

### The switchboard manufacturer as shown on the contract drawings shall integrate and assemble dry type distribution transformers into the switchboard.  The transformer shall be secured in a manner that assures the structural integrity of the vertical switchboard section and the transformer.  Adequate ventilation for the transformer and other installed components shall be provided within the switchboard.

### The switchboard manufacturer shall wire the transformer from the feeder overcurrent device to the line side of the transformer in accordance with UL and the National Electric Code utilizing copper conductors.  The switchboard manufacturer shall wire the secondary side of the transformer to the load or panelboard shown on the drawings in accordance with UL and the National Electric Code utilizing copper conductors.

### Switchboard manufacturer to install vibration dampening device between transformer and support to minimize noise.

## ENCLOSURES

### Integrated Switchboard shall be NEMA 1 Enclosure

## NAMEPLATES

### Engraved nameplates, mounted on the face of the assembly, shall be furnished for all main and feeder circuits as indicated on the drawings.  Nameplates shall be laminated plastic, black characters on white background.  Characters shall be 3/16-inch high, minimum.  Nameplates shall give item designation and circuit number as well as frame ampere size and appropriate trip rating.  Furnish master nameplate giving switchboard designation, voltage ampere rating, short circuit rating, manufacturer’s name, general order number, and item number.  Refer to drawings for actual names and other information.

### Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, lighting contactors, etc., shall be suitably marked for identification corresponding to appropriate designations on manufacturer’s wiring diagrams.

## FINISH

### All exterior and interior steel surfaces of the switchboard shall be properly cleaned and provided with a rust-inhibiting phosphatized coating.  Color and finish of the switchboard shall be ANSI 61 light gray.

## FEEDER CIRCUIT BREAKERS

### Switchboard to be equipped with breakers as shown on the drawings.

### Breakers to be rated for [10,000 AIC] [65,000 AIC] [100,000 AIC].

# EXECUTION

## FACTORY TESTING

### The following standard factory tests shall be performed on the equipment provided under this section.  All tests shall be in accordance with the latest version of ANSI and NEMA standards.

### The switchboard shall be completely assembled, wired, adjusted, and tested at the factory.

#### After assembly, the complete switchboard will be tested for operation under simulated service conditions to assure the accuracy of the wiring and the functioning of the equipment.

#### The main circuits shall be given a dielectric test of 2200 volts for one (1) minute between live parts and ground, and between opposite polarities.

#### The wiring and control circuits shall be given a dielectric test of 1500 volts for one (1) minute between live parts and ground.

### [The manufacturer shall provide three (3) certified copies of factory test reports after shipment if requested at time of order.]

### [The owner’s representative as outlined above shall witness factory tests.

#### Factory witness testing must be requested at time of order.

#### The manufacturer shall notify the owner two (2) weeks prior to the date the tests are to be performed.

#### Transportation, lodging, meals, and incidental expenses shall be the owner’s responsibility.]

## MANUFACTURER’S CERTIFICATION

### A certified test report of all standard production tests shall be available to the Engineer after shipment if requested at time of order.

## TRAINING

### The Contractor shall provide a training session for up to ____ owner’s representatives for ____ normal workdays at a jobsite location determined by owner.

### A manufacturer’s qualified representative shall conduct the training session.  The training program shall consist of instruction on operation of the assembly, circuit breakers, fused switches, and major components of the assembly.

## INSTALLATION

### The Contractors shall install all equipment per the manufacturer’s instructions, contract drawings, and the National Electric Code.

## FIELD ADJUSTMENTS

### The Contractor shall perform field adjustments of the protective devices as required to place the equipment in final operating condition.  The setting shall be in accordance with the approved short circuit study, protective devices evaluation study and protective device coordination study.

### Necessary field settings of devices and adjustments and minor modifications to equipment to accomplish conformance with an approved short circuit and protective device coordination study shall be carried out by the Contractor at no additional cost to the owner.

END OF SECTION