# GENERAL

## SCOPE

### The following section is used to define the requirements for 600 Vac Low voltage motor control centers (MCC’s).  The Contractor shall furnish and install the MCC’s as specified in this section and as shown on the contract drawings.

### This section includes mechanical, electrical and system design features that are being specified for the procurement of safe and reliable MCC’s to meet the specific needs of the project.

## REFERENCES

### The equipment and components in this specification shall be designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/NEMA 250, Enclosures for Electrical Equipment (1000 Volts Maximum)

### ANSI/NFPA 70, National Electrical Code

### CSA C22.2 No. 254-05 General Requirements of Canadian Electrical Code, Part II

### CSA C22.2 No. 14, Industrial Control Equipment

### MIL SPEC TT-C-490, Rev. D, Cleaning Methods for Ferrous Surfaces and Pretreatment for Organic Coatings

### NEMA ICS 1, Industrial Control and Systems: General Requirements

### NEMA ICS 2, Industrial Control and Systems: Controllers, Contactors and Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC

### NEMA ICS 6, Industrial Control and Systems: Enclosures

### NEMA ICS 18- 2001, Motor Control Centers

### NEMA ST 20, Dry Type Transformers for General Applications

### UL 508 Industrial Control Equipment (only for devices included in specification)

### UL 845, Motor Control Centers

### If Arc Resistant MCC are specified in Article 2.03.B6, the MCC’s shall be tested in accordance with IEEE C37.20.7-2007 Type 2 guideline for testing metal enclosed switchgear.

## SYSTEM DESCRIPTION

### The MCC shall be rated at industry standard voltages up to 600V [choose system voltage for specific application ]volt, three phase, [3] [4] wire, [60] [50] Hertz power system having a short circuit availability [65] [100] kilo-amperes RMS symmetrical.

# Specifier Note: It is recommended that all MCCs within any one project be designed at the same fault current rating so starters and other components may be interchange within the facility.

### Wiring shall be NEMA Class [ I ] [ II ], Type [ A ] [ BD ] [ BT ] [ C ].  Where Type C wiring is required, the master terminal blocks shall be located at the [top] [bottom] of the vertical section.  Combination starter units shall be wired out to split type terminal blocks for easy removal of the starter unit without disturbing either factory or field installed wiring.  All control terminal boards shall be accessible from the front.

# Specifier Note: See article by Shahid Sheihk, “NEMA Classification of MCC &Wiring Requirements”   http://apps.geindustrial.com/publibrary/checkout/Classification?TNR=White%20Papers|Classification|generic

## SUBMITTALS

### Approval Submittals:  Manufacturer shall provide electronic copies of the following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26] regarding Electrical equipment:

#### Wiring diagrams

#### Unit summaries which includes details of starter and feeder units including disconnect type, amperage, size, control devices, and electrical devices

#### List of deviations from contract documents and requests for clarifications of specification documents and/or drawings.

#### Elevation drawings with conduit entry space availability including enclosure types and system ratings

#### Recommended spare parts list

### Record Drawings:  Manufacturer shall provide electronic copies of the following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26] regarding Electrical equipment:

#### The manufacturer shall provide a copy of the drawing that reflect the “for-installation” state of the equipment when shipped from the factory

#### The drawings shall be in [pdf] [dxf] format.

#### The final drawing package shall be marked as “for-installation”

#### Field modifications not covered by manufacturer’s warranty, by Contractor shall be the responsibility of the Contractor.  Drawings shall document all changes made during installation and commissioning. All manufacturer errors or omissions found during commissioning shall be documented by the manufacturer. If drawing changes are required by Manufacturer, the contractor shall be responsible for ensuring those are provided.

#### [Certified Factory test reports shall be provided with “for-construction” documentation]

#### [A Certificate of Compliance for UL 845 shall be provided with for-construction documentation]

## INSTALLATION, OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide [3] [digital] copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division [1] [01] and Division [16] [26].

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of low voltage motor control centers for over [30] years.

### Low voltage motor control centers shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.02 of this specification.

### Vertical sections and individual units shall be UL Labeled

### Motor control centers shall be qualified for use in seismic areas as follows:

#### High seismic loading as defined in IEEE Std 693-2005, with 1.3 amplification factor.

Note to Specifier: For more information please see http://apps.geindustrial.com/publibrary/checkout/DET-463H?TNR=Application%20and%20Technical|DET-463H|generic

#### IBC-2012, Ss = 2.69g, Sds = 1.40g, Ip = 1.5, for all z/h equal to 1 Ss = 3.98g, and Sds = 2.65, Ip = 1.5, for z/h equal to 0 in accordance with ICC-ES-AC156.

#### Seismic compliance shall be qualified only through shake table testing.  Compliance by calculation is not acceptable.

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Manufacturer shall ship no more than three motor control sections in individual shipping splits for ease of handling. Contractor shall coordinate with manufacturer the shipping splits required for the equipment and manufacturer shall show the location of shipping splits on factory drawings.

### Each shipping split shall be mounted on shipping skids and wrapped for protection and be equipped with removable shipping [angles] [eyes] to aide in lifting.

### Contractor shall inspect and report concealed damage to carrier within 48 hours regardless of the contractual shipping terms.

### If storage is necessary, Contractor shall store in a clean, dry space. Cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic. It is the responsibility of the Contractor to heat enclosures to prevent condensation during storage as required to protect equipment.

### Contractor shall handle in accordance with manufacturer's recommendations to avoid damaging equipment, installed devices, and finish. Lift only by installed lifting [eyes][angles].

### For international shipping by air or by boat, Contractor must properly export pack the MCC to avoid damage during transit.

### MCC should never be placed on its side, back or any other position other than floor standing upright.  Doing so could jeopardize the integrity of the bus and bus bracing.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Contractor shall order MCC enclosure to match the existing conditions and equipment protection required for the environment at the site of the installation.

### Motor control centers shall be located in well - ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus 30 and plus 40 degrees C. MCC shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer shall warrant equipment to be free from defects in materials and workmanship for 1 year from date of energizing or 18 months from date of shipment, whichever occurs first.

## FIELD MEASUREMENTS

### Contractor shall make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

### If MCC is replacing existing equipment, Contractor shall provide manufacturer with drawings for the existing installed equipment, location of existing conduit locations and field measurements where required to ensure a functional replacement. Add to existing MCC shall be provided by the same manufacturer as the original equipment. Unless the original manufacturer indicates in writing it is not possible, connections between new and older installed sections shall be via hard bus and not cabled.

# PRODUCTS

## MANUFACTURER

### General Electric Company products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.  The following equipment shall be provided:

### GE Evolution E9000 MCC

### _______________________

### _______________________

## RATINGS

#### Power shall be distributed by means of a continuous horizontal bus with a current rating of [600] [800] [1200] [1600] [2000] [2500] amperes.  If required on the one line diagrams a neutral bus shall be provided rated at [50%][100%] of phase conductors.

#### The main bus shall be [tin-plated] [silver-plated] copper.

#### The main bus shall be braced for [65,000][100,000] amperes RMS symmetrical.

#### The main bus shall be isolated by barriers from wire troughs, starters, and other areas.

#### There shall be double bolt connections on main bus joints and splice connections.  Main bus splicing between shipping splits shall be accomplished with no structural disassembly. For easier access, top cover shall be removable.

#### The main bus shall be fully rated and arranged for future extension.

#### The vertical bus in each section shall be rated [300] [600] [850]amperes and shall be [tin-plated] [silver-plated].

### Specifier Note: 850A vertical bus requires 1200A or greater main bus.

#### The vertical bus shall have a flame-retardant polyester-glass insulation / isolation system.  This system shall insulate the vertical bus front and rear.  In addition, the barrier shall isolate each phase bus. Openings in the vertical bus insulation/isolation system shall permit the entry of unit stabs.  Unused openings shall have plugs or covers to prevent the entry of foreign objects.

#### [The openings in the vertical bus used for starter connections shall be covered by an automatic shutter mechanism.  The shutters shall automatically cover the openings when the starter is removed.]

#### The vertical bus shall be braced to the same short circuit rating as the main horizontal bus.

#### A copper ground bus shall extend the full width of the motor control center.  The ground bus shall be rated [300] [600] amperes.  The ground bus shall be drilled for [6] or [___] mounting holes for ground lugs. Lugs shall be furnished as specified.

#### [There shall be a vertical copper ground bus in each section. The ground bus shall be accessible to a bus stab mounted in the unit compartment area and arranged so that the unit ground stab engages before the power stabs engage the vertical bus.] [A motor load ground lug shall be mounted in the starter unit and used for terminating the ground of multi-conductor cables.]

#### A neutral bus shall be furnished when shown on the plans. [incoming section only] [full-width of line up] The neutral bus shall be [100%] [50%] of main bus amperes. Lugs of the proper current rating shall be furnished.

## CONSTRUCTION

### Refer to Contract Drawings for actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; interrupting and withstand ratings of devices, buses, and components; and other required details.

### Enclosure

#### Indoor enclosures shall be NEMA Type [1] [1-Gasketed] [2] [12].

#### Outdoor enclosures, where indicated on drawings, shall be NEMA [3R Non-Walk-In]. Wind load shall be qualified through 130 mph.

#### Each motor control center shall consist of the required number of vertical sections of heavy gauge sheet steel bolted together to form a rigid self- supporting assembly.  A removable lifting angle shall be mounted to the motor control center at the top.  Removable bottom channel sills shall be mounted front and rear of the vertical sections and shall extend the width of the lineup.

#### Vertical sections shall be nominally 90-inch high with additional 1.5-inch floor sills and [20] [13]-inch deep. [If 1600A or greater, the vertical sections shall be 22-inch deep]. Alternate section widths with vertical bus may be 24-inches or 30-inches wide when required. When there is no vertical bus, the maximum width shall be 36-inches

#### Specifier Note: Alternate heights available starting at 66-inches, contact factory for details. Alternate section widths with vertical bus shall be 24-inches or 30-inches wide when required. When there is no vertical bus, the maximum width shall be 36-inches.

#### Each vertical section shall be equipped with vertical side barriers to prevent faults from traveling easily between adjacent sections.

Specifier Note:  Include this next section if Arc Resistant Enclosure is required.

#### Arc Resistant Enclosures shall meet the following requirements

##### MCC shall be arc resistant up to 65kA, bolted fault current at 480V [600V].

##### Arc resistant rating shall be for a minimum of 6 cycles at full current.

##### Arc resistant rating shall require the use of a plenum to channel arc effluent to a remote area.

##### Arc resistant rating shall apply with a starter in the disconnected or connected position if it is still installed in the MCC.

##### Equipment must be Type 2 Arc Resistant equivalent.

##### Arc resistant rating shall be tested and certified by manufacturer based on applicable sections of IEEE/ANSI C37.20.7 guide for arc resistant testing of Type 2 accessibility rating, where applicable to low voltage motor control centers.

### Wireways

#### Each vertical section shall contain a minimum 12-inch high top horizontal wireway and a 6“bottom wireway. When loads exit the bottom a 12” bottom wireway shall be provided. A removable hinged door with ¼ turn latches shall cover the horizontal wireway. [Vertical wireway can be increased by 4-inches to expand spacing for wires.]

#### A separate vertical wiring trough shall be furnished in each vertical section adjacent to plug-in unit.  The wire trough shall permit the installation of field wiring and shall isolate this wiring from the adjacent unit.  No terminal blocks shall be located in the vertical wireway.   Cable tie supports shall be furnished in the vertical wireway to hold cable and wiring in place. A removable hinged door shall cover the vertical wiring trough.

#### [If communication wiring is required, a metal shielding shall be added in the vertical wiring trough to provide isolation from power and control wiring within the vertical wiring trough.]

### Incoming Power / Main Protective Device

#### Incoming power to the motor control center shall be [cable] [bus duct].

##### [Incoming power cables shall enter the [top] [bottom] of the motor control center.]  [Incoming cables shall be of the size and number shown on the plans.]

##### [Incoming bus duct shall enter the top of the motor control center and shall have a current rating as shown on the plans.]

#### The main protective device where indicated on the drawings or schedules shall be a molded case circuit breaker for current ratings up to 1200A, a stored energy type (insulated case) circuit breaker for current ratings greater than 1200A].  If a fused switch is shown on the one line diagram the switch shall be UL 977 listed. The main device shall have a current rating as shown on the plans and shall have an interrupting rating equal to or greater than the available short circuit current. Provide main device as specified in the appropriate part of this article below.

#### When a main overcurrent device is shown in the drawings the circuit breaker or switch shall have the following characteristics:

##### When called for in the one line diagram main circuit breakers rated 1200A and below may be molded case type, UL 489 listed. Short circuit rating shall be equal or higher than that of the MCC. Circuit breaker shall be provided with a fully adjustable trip unit with adjustable Long Time Pickup, Short Time Pickup and Instantaneous Pickup. Long time curves shall be available in at least two shapes, one approximating an I2t delay and the other an I4t delay curve. Short time protection function shall include adjustable time delays and shall include at least three curve shapes; definite time, I2t slope and I4t slope. The instantaneous adjustment shall be sufficient to provide full selective coordination with all branch devices within the MCC up to the full short-circuit rating of the MCC. If this is not possible the main circuit breaker furnished shall be a Low Voltage Power Circuit Breaker, UL 1066 listed, with sufficient withstand rating to adjust the instantaneous protection to achieve full selective coordination with all branch devices. If branch devices are rated 400A or above the branch devices and the main device shall implement zone selective interlocking to ensure the fastest possible protection will remaining selective. No deviations from the requirement for full selective coordination will be accepted.

##### When shown on the one line diagrams main circuit breakers rated above 1200A shall be molded case stored energy type (insulated case), UL 489 listed. Or they may be Low Voltage Power Circuit Breakers, UL 1066 listed. Short circuit rating shall be equal or higher than that of the MCC. Circuit breaker shall be provided with a fully adjustable trip unit with adjustable Long Time Pickup, Short Time Pickup and Instantaneous Pickup. Long time curves shall be available in at least two shapes, one approximating an I2t delay and the other an I4t delay curve. Short time protection function shall include adjustable time delays and shall include at least three curve shapes; definite time, I2t slope and I4t slope. The instantaneous adjustment shall be sufficient to provide full selective coordination with all branch devices within the MCC up to the full short-circuit rating of the MCC. If this is not possible the main circuit breaker furnished shall be a Low Voltage Power Circuit Breaker, UL 1066 listed, with sufficient withstand rating to adjust the instantaneous protection to achieve full selective coordination with all branch devices. If branch devices are rated 400A or above, these branch devices and the main device shall implement zone selective interlocking to ensure the fastest possible protection will remaining selective. No deviations from the requirement for full selective coordination will be accepted.

##### A fusible switch main device shall be provided when called for in the one line diagram. The switch shall be UL 977 listed. The switch shall be electrically operated. Shall include class L fuses as defined by the coordination study. Three spare fuses shall be provided. If a main fusible switch is shown on the one line diagram and the manufacturer cannot provide a UL 977 listed switch that is able to be electrically operated then 3.b above shall be provided with additional class L current limiting fuses downstream of the circuit breaker per the fuse requirements of the one line diagram and coordination study.

##### The MCC design shall have an ability to reduce the incident energy at the main section during maintenance in one of the following ways:

###### Circuit breaker trip unit or switch control relay unit shall implement a maintenance switch function that allows an instantaneous protection setting, separately adjustable, to be set via an external signal to the circuit breaker trip.  The function shall be implemented such that it operates from a separately mounted three position switch. The switch positions shall be “Normal or Off” (maintenance instantaneous disabled), “Test” (used to test control power circuitry and signal wiring), and “ON” (which is used to enable the maintenance instantaneous protection). The switch shall include indicating light(s) to indicate that the test function is working properly and that the additional protection has been enabled at the trip unit (positive feedback). When the maintenance instantaneous protection is turned “off” the protection shall delay at least 15 seconds before it goes back to normal protection. If the trip unit or relay does not provide that delay a separate timing control shall be installed to provide at least a 15 second off delay for the maintenance switch function. If a main fusible switch is shown on the one line diagram and the manufacturer cannot provide a UL 977 listed switch that is able to implement the maintenance instantaneous function then a circuit breaker per articles 3.a or 3.b above shall be provided with additional class L current limiting fuses downstream of the circuit breaker per the fuse requirements of the one line diagram and coordination study.

(2)	Or approved equal

### Where indicated on the drawings, the motor control center shall be provided with an incoming transition section for close coupling with GE switchgear, switchboard or transformer.

## COMPONENTS

### User Metering

#### Provide a UL listed and digital multifunction power monitor.  The monitor case shall be fully enclosed and shielded

#### The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

##### The Monitor shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.  Isolation shall be no less than 2500V AC.

##### Surge withstand shall conform to IEEE C37.90.1,62.41 and IEEE 1000-4

##### Shall have a standard ANSI C39.1 case mount.

#### The Monitor shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral; real power, reactive power, apparent power, power factor and frequency.

##### The Monitor must be capable of providing readings for both instantaneous and average readings.

##### The Monitor must also be capable of providing all single phase real, apparent, reactive power and power factor values.

##### The Monitor shall record and store total bi-directional energy. It shall include separate registers for positive and negative energy.

##### The Monitor shall record and store total bi-directional accumulated energy and total accumulated apparent energy.

##### The Monitor shall monitor max/min average demand values for all current and power readings. The demand interval shall be user programmable.  [Maximum and minimum values shall be stored with a date/time stamp.]

Specifier Note: Please choose one of the following additional feature sets as required.

Specifier Note:  The following reflects capabilities of the GE EPM6000 for more information please see: https://www.gedigitalenergy.com/multilin/catalog/epm6000.htm:

#### The Monitor shall have an accuracy of +/- 0.1% or better for volts and amps, and 0.2% for power functions, and shall meet IEC687 (0.2%)

##### The monitor shall include a three line, integrated, light-emitting diode (LED) display.

###### The Monitor must be capable of displaying one leg of volts, amps and total power simultaneously.

###### The display shall provide user access to all phase voltages (phase to neutral and phase to phase), currents (phase and neutral), watts, VARs, VA, power factor, frequency and kwh

###### The display must provide user access to max/min values for all displayed quantities.

###### The display shall have a % load bar display for ease of full load viewing

##### The monitor shall be microprocessor based and shall be fully user programmable.

##### [The monitor shall be provided with an RS485 digital communications port. The Monitor shall communicate using a MODBUS RTU protocol and shall have a communication baud rate of at least 57k.]

##### [The monitor shall be provided with one KYZ pulse outputs]

Specifier Note:  The following reflects capabilities of the GE EPM7000. For more information please see: https://www.gedigitalenergy.com/multilin/catalog/epm7000.htm

#### The monitor should have an accuracy of %0.2 or better, and %0.1 for voltage and current.

##### The meter should meet ANSI C 12.20 and IEC 687 standards.

##### The meter must be able to sample at 400+ samples per cycle on all channels measured readings simultaneously and record events up to 512 samples/cycle.

##### The meter must be capable of logging up to 4MB of data in order to retrieve archived data, capture past events, and analyze disturbances.

##### The meter shall provide limits alarms and control capabilities, limits can be set for any measured parameter, up to 16 limits per parameter can be set, limits shall be based on % of full scale settings, manual relay control should be available thru software.

##### The monitor shall include a three line, integrated, light-emitting diode (LED) display.

###### The Monitor must be capable of displaying one leg of volts, amps and total power simultaneously.

###### The display shall provide user access to all phase voltages (phase to neutral and phase to phase), currents (phase and neutral), watts, VARs, VA, power factor, frequency, %THD, %load bar and kwh.

###### The display must provide user access to max/min values for all displayed quantities.

###### The display shall have a % load bar display for ease of full load viewing.

##### The meter must allow voltage input measurements up to 416 Volts Line to Neutral and 721 Volts Line to Line.

##### The meter must be able to provide data to RTUs, PLCs, and other control devices.

##### The monitor shall be provided with an RS485 digital communications port. The Monitor shall communicate using a MODBUS RTU or ASCII protocol and shall have a communication baud rate range of 9600-57k.

##### The meter shall have I/O expandability through two option card slots on the back, the cards shall be capable of being installed in the field, without removing the meter from installation.

##### The meter must be able to be connected via Serial, Ethernet, or Modem.

##### [Meter option with Ethernet card, capable of web server that will be viewable by internet browsers.]

##### The meter shall have data-logging capability with the 2, 3, and 4 Megabyte memory upgrade (Upgrade packs B-F). The meter shall have a real-time clock allows for time stamping of all the data in the meter when log events are created.

##### The meter shall provide %THD (% of total Harmonic Distortion). Harmonic magnitude recording to the 40th order shall be available for voltage and current harmonics.

##### The meter shall provide a simultaneous voltage and current waveform recorder.

##### The meter shall be capable of recording 512 samples per cycle (waveform) for voltage sag or swell or a current fault event.

##### The monitor shall be provided with one KYZ pulse outputs

Specifier Note:  The following reflects capabilities of the GE PQMII meter. For more information please see: https://www.gedigitalenergy.com/multilin/catalog/pqmii.htm:

#### The Monitor shall have an accuracy of +/- 0.2% or better for volts and amps, and 0.4% for watts.

##### Voltages and currents shall be sampled at 64 samples per cycle.

##### The Monitor shall have up to 1MB of non-volatile RAM for data trending and waveform capture.

###### The monitor shall be capable of retaining historical data in a non-volatile memory with a programmable number for a single parameter. The user can select any combination of values to be stored.

###### Interval of snapshots shall be triggerable on programmable changes of state of voltage and current.

###### The Monitor shall store waveform events for all 6 channels of voltage and current for a minimum of 100 events. Each event will consist of readings of 60 cycles, 10 cycles prior to the event, and 50 cycles past the event.

###### Event recording shall be triggered when the RMS of voltage or current exceeds user programmable high-speed set points.

###### The Monitor must be able to record each of the channels of voltage or current per event if the event continues past the initial 60 cycles. Recording duration set-point shall be programmable.]

##### The Monitor shall have three serial communication port; 1 RS232C and 2 RS485.  Ports must be capable of communicating simultaneously to different devices.

##### The Monitor shall communicate using  a MODBUS RTU or DNP open protocol and support communications baud rates of up to 19.2K

##### The Monitor shall calculate the harmonic signature, %THD and K-Factor for all voltage and current inputs with valid data for harmonic spectrum capability to the 32nd harmonic.

##### The Monitor must be capable of capturing a graphic image of the waveform for each of the 6 channels of Voltage and Current and make it available in a RAM buffer for retrieval through the digital communication port.

Specifier Note: The following capabilities are furnished on GE EPM9650Q meter. For more information please see: https://www.gedigitalenergy.com/multilin/catalog/epm9650.htm

##### The monitor shall have the following minimum accuracy requirements.

###### Voltage accuracy shall be within less than 0.01% for the 1 second readings and less than 0.1% for the100 millisecond readings.

###### Current accuracy shall be within less than 0.025% for the 1 second readings and less than 0.1% for the 100 millisecond readings.

###### Power and energy accuracy shall be within less than 0.04% at unity PF and within 0.06% at 0.50 PF.

###### Frequency accuracy shall be within less than 0.001 Hz.

###### Power meter shall meet ANSI C12.20 and IEC 687 accuracy requirements.

##### Power meter shall provide multiple digital communication ports and support multiple open protocols.

###### Meter shall include four (4) independent, digital communication ports. Each port shall be RS-485 architecture. Port 1 shall be user selectable as either RS-232 or RS-485 architecture.

###### Each port shall be user configurable with regard to speed, protocol, address, and other communications parameters. All ports shall support a maximum communication speed of 115k baud simultaneously.

###### One communication port shall be configurable as either a Master or a Slave port. The Master configuration shall enable the unit to act as an RTU and interface with other Modbus devices and EI I/O Modules communicating using Modbus RTU protocol.

###### Meter shall offer both Modbus and DNP 3.0 open protocols as standard configurations. All instantaneous data, logged data, event data, power quality analysis and waveform information shall be available using these open protocols.

##### Meter shall have at least eight high-speed status inputs for capturing external events.  All high-speed status inputs shall be monitored at a user set rate from 1 to 8 samples per millisecond.  All changes in status shall be time stamped to the nearest millisecond and placed in an event log with time and event label information.

##### Power meter shall provide a separate IRIG-B input for time synchronizing to GPS time signal.  IRIG-B input shall accept un-modulated time signal input from a standard GPS satellite clock.

##### Power meter shall be equipped with 4MB of non-volatile RAM for recording logs and programming information.

###### Meter shall store historical trending data, power quality data, and waveform recordings in memory.

###### In the event of loss of control power, data stored in memory shall be retained for at least 10 years.

###### Memory shall be allocated to the various logging functions required. All logging features required shall be simultaneously available at the specified levels. Exercising any one feature at the specified level shall not limit exercising of any or all other features to their full, specified level.

###### Meter shall store all programming and set-up parameters in non-volatile memory. In the event of loss of control power, meter programming data stored in memory shall be retained for at least 10 years.

##### Power meter shall measure and record the magnitude and phase angle of all harmonics through the 127th for all voltages and currents. Meter shall provide %THD and K-Factor for all channels.  All harmonic values shall be available through the digital communications ports in real time.

##### Power meter shall capture and record all CBEMA quality events.  CBEMA events shall be date/time stamped to the millisecond. Entries to CBEMA log shall include date/time stamp, duration, and magnitude information. The CBEMA log shall be downloadable through the digital communications ports.

##### Power meter shall capture and record out-of-limit conditions in a log. Entries to Limits log shall be made anytime a monitored quantity exceeds the user set limit assigned to that quantity.  Entries to the Limits log shall be time stamped to the millisecond and include the measured quantity value and label.

##### Power meter shall provide waveform recording to capture and record transients and quality problems on current and voltage waveforms.  Meter shall sample waveform at a user configurable rate of 16 to 512 samples per cycle (60Hz cycle).

###### Meter shall hold at least 96 records of waveform recording in non-volatile memory. Each record shall be a minimum of 8 cycles in duration at the highest sample rate or 64 cycles in duration at the lowest sample rate.  Each waveform record shall include pre-event and post-event data.

###### A waveform record shall be taken whenever the RMS value of voltage or current exceeds user-set limits or a status change occurs on any one of the eight high-speed status inputs.

##### The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

###### The Monitor shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.  Isolation shall be no less than 2500V AC.

###### Surge withstand shall conform to IEEE C37.90.1,62.41 and IEEE 1000-4

###### Shall have a standard ANSI C39.1 case mount.

##### The Monitor shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral; real power, reactive power, apparent power, power factor and frequency.

###### The Monitor must be capable of providing readings for both instantaneous and average readings.

###### The Monitor must also be capable of providing all single phase real, apparent, reactive power and power factor values.

###### The Monitor shall record and store total bi-directional energy. It shall include separate registers for positive and negative energy.

###### The Monitor shall record and store total bi-directional accumulated energy and total accumulated apparent energy.

###### The Monitor shall monitor max/min average demand values for all current and power readings. The demand interval shall be user programmable.  [Maximum and minimum values shall be stored with a date/time stamp.]

##### The Monitor shall have an accuracy of +/- 0.2% or better for volts and amps, and 0.4% for watts.

##### Voltages and currents shall be sampled at 64 samples per cycle.

##### The Monitor shall have up to 1MB of non-volatile RAM for data trending and waveform capture.

###### The monitor shall be capable of retaining historical data in a non-volatile memory with a programmable number for a single parameter. The user can select any combination of values to be stored.

###### Interval of snapshots shall be triggerable on programmable changes of state of voltage and current.

###### The Monitor shall store waveform events for all 6 channels of voltage and current for a minimum of 100 events. Each event will consist of readings of 60 cycles, 10 cycles prior to the event, and 50 cycles past the event.

###### Event recording shall be triggered when the RMS of voltage or current exceeds user programmable high-speed set points.

###### The Monitor must be able to record each of the channels of voltage or current per event if the event continues past the initial 60 cycles. Recording duration set-point shall be programmable.]

##### The Monitor shall have three serial communication port; 1 RS232C and 2 RS485.  Ports must be capable of communicating simultaneously to different devices.

##### The Monitor shall communicate using  a MODBUS RTU or DNP open protocol and support communications baud rates of up to 19.2K

##### The Monitor shall calculate the harmonic signature, %THD and K-Factor for all voltage and current inputs with valid data for harmonic spectrum capability to the 32nd harmonic.

##### The Monitor must be capable of capturing a graphic image of the waveform for each of the 6 channels of Voltage and Current and make it available in a RAM buffer for retrieval through the digital communication port.]

### Units

#### Combination motor controller and feeder units shall employ [molded case circuit breakers] [fusible switches with clips for [J or R type fuses] for branch circuit protection.  Circuit breaker disconnects for combination motor starters shall be [thermal-magnetic] [magnetic only].

#### All combination starter and feeder units of plug-in construction shall utilize a positive guidance system to insure positive connection of the unit stabs to the section vertical bus.  Insertion and removal of each unit shall not require the use of special tools.

#### Unit shelves shall be of a lift out design, so that the shelf may be removed without the use of special tools.

#### Connection from the power stabs to the unit disconnect shall be a direct connection.

#### Each circuit breaker starter unit size 1 through size 5 shall be of plug-in construction.  Each feeder breaker rated 600A or less shall be plug-in construction.

#### Each unit compartment shall be equipped with a flange-formed pan type door.  The door shall be mounted on the vertical section with removable hinge pins.

#### Each unit shall be equipped with an operating handle. The handle shall be connected to the disconnect operator using a direct drive and requiring no adjustments of linkage.

#### The handle shall be mechanically interlocked with the door preventing it from opening with disconnect closed. The interlock shall also prevent disconnect being closed with door open. The interlock shall be capable of being defeated allowing the door to be opened with disconnect closed or disconnect closed with the door open.

#### The unit handle shall have provision to padlock in the off position.  On circuit breaker units the handle shall have a "tripped" position in addition to OFF/ ON.

#### Each unit shall be capable of being padlocked in a partially withdrawn position.  In this position, the unit power stabs are disengaged from the vertical bus and no power can enter the unit.

#### Combination starter units specified with Type B or C wiring shall be supplied with split-type control terminal blocks. The terminal blocks shall be front mounted and shall allow the removal of the unit without disconnecting any of the control wiring. Combination starter units up to size 5 shall be plug-in construction and shall be capable of being removed without disconnecting any control leads from their terminal blocks.

#### Overload relays shall be:  (Specifier: Please select one of the following)

##### [Bimetallic, non-ambient compensated]

##### [Bimetallic, ambient compensated]

##### [Solid-state, ambient insensitive, self-powered, including adjustable FLA, phase unbalance, phase loss protection, selectable overload class (10, 20, 30), with 2% accuracy and  repeatability, built-in thermal memory to prevent hot motor starts, isolated 1NO and 1 NC auxiliary contacts.]

##### [Advanced microprocessor based motor protection as described in Article 2.03. I.]

#### Control power for starter units shall be from: (select one)

##### [Individual control power transformers shall be furnished in each starter unit.  One secondary lead shall be furnished with a fuse and the other lead shall be grounded.  Control power primary fuses are required].

##### [A separate source (common control) Two-wire terminal points shall be provided. One leg shall be wired through normally open auxiliary contacts in each disconnect and a control power fuse rated 1 amp shall be provided.

#### Starter units shall be provided with the following auxiliary devices:

##### [auxiliary starter interlocks,  ______ N/O, ______N/C].

##### [control / timing relays (as shown on the drawings)].

##### [door mounted pilot devices shall be 30mm heavy duty:

###### start-stop pushbutton

###### H-O-A selector switch

###### Indicating lights (quantity and color).  Indicating lights shall be [full voltage] [reduced voltage transformer] [push to test] [incandescent] [LED] type.

### SPECIFIER NOTE: Include this section 15 if Engineer requires additional safety features associated with IEEE 1683 guidelines.nits with Arc Flash Mitigation (AFM) shall be designed to provide safety features in attempt to decrease the likelihood of maintenance personnel coming in contact with live parts or being exposed to an arc flash event.  All stab-in units shall be available with these features or characteristics. Units shall include but are not limited to FVNR, FVR, ASTAT, VFD, SPD and Feeder units up to 600A.  Units shall have the following features:

#### Retractable stabs: All units shall be constructed so that each unit can be inserted and withdrawn from the vertical bus while the unit door is closed.

##### Closed door stab and shutter position indication

###### External visual indication of the position of the stabs within the unit shall be provided.

###### Green indicating that the stabs are mechanically withdrawn and not engaged into the vertical bus.

###### Red indicating that the stabs are mechanically inserted into the vertical bus and voltage is likely to be present at the stabs.

#### Specifier Note: A door mounted voltage indicating device is recommended, but is optional. If desired the article below describes it. Delete if not desired.

##### [A door mounted sensing device that indicates voltage present at the load side of the circuit breaker, motor protector or switch and/or at the unit stab shall be provided. Device as provided by Voltage Vision or equal].

##### Mechanical Safety Interlocks:

###### Safety interlocks that prevent the unit from being inserted into or removed from the structure when the stab is in the extended or engaged position.

###### Safety interlocks that prevent the unit from being racked in or out of the structure with the disconnect in the “on” position.

###### Additional provision for padlocking shall be available to prevent the unit from insertion into the connected position during maintenance.

#### Specifier Note: A remote racking device is recommended, but is optional. If desired the article below describes it. Delete if not desired.

##### Remote Racking

###### A separate remote racking device shall be available to allow the units to be racked in and out of the vertical bus from 40 feet away.  Quantity _______ of these racking devices shall be included in [each MCC] [project]. The remote racking device shall be operated at 110Vac.

Specifier Note: The next section contains options available to prevent incidental contact. Choose as many of these features as desired by user.

#### [IP20 features and preventing incidental contact with live parts]

##### [If fuses are used within the unit, fuses shall be IP20 protected fuses.]

##### [Barriers shall be provided on the load side of the unit disconnect to prevent unwanted contact with the disconnect load terminals. Covers shall have sufficient opening for test probes required for trouble shooting control operations and designed to allow the user to infrared scan the load terminals.]

##### [The starter contactor shall either have IP20 provision for the exposed terminals or adequate barriers to prevent incidental contact with live parts.]

#### Infrared scanning ports at section

##### Infrared scanning ports shall be available for each vertical section for infrared scanning of the main horizontal bus joints and where the vertical bus connects to the horizontal bus.

##### Infrared scanning ports shall be available at each unit to view [load side of circuit breaker terminals] or [load side of overload terminals].

Specifier Note: One racking device shall be included for each electrical room that contains at least one MCC.

### Stored Energy (Insulated Case), UL 489 Circuit Breakers.

#### Stored Energy, UL 489, circuit breakers shall be individually mounted.

#### Main and tie breakers shall be [manually] [electrically] operated, stationary mounted.

Specifier Note:  Electrically operated stored energy devices are always suggested for mains and ties so that CBs can be remotely operated for greater user safety.

#### Circuit breakers shall be constructed of a high dielectric strength, glass reinforced insulating case. The interrupting mechanism shall be arc chutes. Steel vent grids shall be used to suppress arcs and cool vented gases. Interphase barriers shall to isolate completely each pole.

#### Circuit breakers shall contain a true two-step stored energy operating mechanism which shall provide quick make, quick break operation with a maximum five cycle closing time. Circuit breakers shall be trip free at all times. All poles shall trip together.

#### Stored Energy circuit breakers shall be rated to carry 100 percent of their frame ampacity continuously.

#### A charging handle, close push-button, open push-button, and Off/On/Charge indicator shall be located on the circuit breaker escutcheon and shall be visible with the circuit breaker compartment door closed.

#### Circuit breaker digital electronic trip units shall be as described in Article 2.03G.

### Molded Case Circuit Breakers for use as mains, ties and feeders rated 400A and larger, up to 1200A.

#### Furnish GE Spectra RMS™ Molded Case Circuit Breakers or equal

#### Main circuit breaker shall be connected to the vertical bus by bolted connections.

#### Feeder circuit breakers up to 600A shall be provided in a plug-in unit for connection to the MCC vertical bus.

#### Circuit breaker frames shall be constructed of a high-strength, molded, glass-reinforced polyester case and cover. Circuit breakers shall have an over-center, toggle handle-operated, trip free mechanism with quick-make, quick-break action independent of the speed of the toggle handle operation. The design shall provide common tripping of all poles. Circuit breakers shall be suitable for reverse feeding.

#### Circuit breaker plug-in units shall be provided with an external operating handle which shall have ON and OFF position clearly marked on on the outside of the circuit breaker enclosure.

#### Circuit breakers shall include factory installed mechanical lugs. Lugs shall be UL listed and rated 75 or 60/75 degrees C as appropriate. Circuit breakers shall be 80 percent rated.

#### Circuit breakers shall use digital true RMS sensing trip units.

#### [Each main or feeder circuit breaker with a frame size 400 amps and larger shall have digital electronic trip units as described in Article 2.03.H.]  [Circuit breaker digital electronic trip units shall be as described in Article 2.03H.]

### Digital Electronic Trip Unit for stored energy Circuit Breakers and molded case circuit breakers 400A and larger.

#### Each circuit breaker shall be equipped with a digital electronic trip unit. The trip unit shall provide protection from overloads, [and] short circuits [and ground faults]. The protective trip unit shall consist of a solid state, microprocessor based programmer; tripping means; current sensors; power supply and other devices as required for proper operation.  Furnish GE Entelliguard TU digital electronic trip units or equivalent as specified below.

#### As a minimum, the trip unit shall have the following protective functions unless otherwise indicated on the drawings:

##### adjustable current setting or long time pickup;

##### adjustable long time delay in two shapes, approximate I2t shape and straight line I4t shape.

##### switchable, adjustable short time pickup and delay with at least three shapes; definite time, I2t and I4t.;

##### adjustable instantaneous pickup; Instantaneous pickup adjustability of mains and ties shall be sufficient to ensure full selective coordination with all branch devices.

##### [adjustable ground fault pickup and delay] [Where indicated on the drawings provide GF alarm only function]

##### Main circuit breaker trips 800A and above or switch control relay units for main switches rated 800A and above shall implement a maintenance switch function that allows an instantaneous protection setting, separately adjustable, to be set via an external signal to the circuit breaker trip.  The function shall be implemented such that it operates from a separately mounted three position switch. The switch positions shall be “Normal or Off” (maintenance instantaneous disabled), “Test” (used to test control power circuitry and signal wiring), and “ON” (which is used to enable the maintenance instantaneous protection). The switch shall include indicating light(s) to indicate that the test function is working properly and that the additional protection has been enabled at the trip unit (positive feedback). When the maintenance instantaneous protection is turned “off” the protection shall delay at least 15 seconds before it goes back to normal protection. If the trip unit or relay does not provide that delay a separate timing control shall be installed to provide at least a 15 second off delay for the maintenance switch function. If a main fusible switch is shown on the one line diagram and the manufacturer cannot provide a UL 977 listed switch that is able to implement the maintenance instantaneous function then a circuit breaker per articles 3.a or 3.b above shall be provided with additional class L current limiting fuses downstream of the circuit breaker per the fuse requirements of the one line diagram and coordination study.

##### As a minimum, the trip unit shall include the following features:

##### Long time and short time protective functions, if provided, shall have true RMS sensing technology and thermal long time memory, also known as a cooling circuit or algorithm.

##### Ground fault protective function, if provided, shall contain a memory circuit to integrate low level arcing fault currents with time, to sum the intermittent ground fault spikes.

##### High contrast liquid crystal display (LCD) unit shall display settings, trip targets, and the specified metering displays.

##### Multi-button keypad to provide local setup and readout of all trip settings on the LCD.

##### An integral test jack for testing via a portable test set and connection to a battery source.

##### A mechanism for sealing the trip unit.

##### Noise immunity shall meet the requirements of IEEE C37.90.2.

##### Display trip targets for long time, short time, and ground fault, if included.

##### The trip unit shall keep a log of the last ten events including overcurrent trips, protective relay trips.  The log shall store RMS currents, phase, type of trip, trip counter, time and date for each event.

##### Instantaneous trip shall utilize an algorithm which permits fully selective operation with downstream current limiting devices up to the short time rating of the circuit breaker, when the instantaneous pickup is set above the current limiting threshold or per the manufacturer’s selectivity documentation.

SPECIFIER NOTE:  Include the following for communications

##### [The trip unit shall include Modbus RTU communication capability.  The trip unit, through dedicated secondary terminals on the breaker, shall provide a communication port for communication with and access to a remote computer.  All metering, set points, protective-trip counts, and other event signaling shall be retrievable by the remote computer.]

#### The trip unit shall include the following metering functions, which shall be displayed on the LCD (if the manufacturers trip unit can not incorporate the specified functions, separate device(s) with equal function shall be provided for each breaker):

##### Current, RMS, each phase;

Specifier Note:  Include the following for metering option.

##### [Voltage, RMS (V), line-to-line or line-to-neutral.

##### Energy (kWh, MWH, GWH), each phase and total, user resettable.

##### Peak Power Demand (KW, MW), user resettable.

##### Real power (KW, MW), each phase and total.

##### Reactive power (KVAR, MVAR), each phase and total.

##### Apparent power (KVA, MVA) , each phase and total

##### Frequency (Hz).

##### Power factor.

##### Waveform capture capability.  Upon triggering, a total of eight cycles of voltage (each phase) and current (each phase) shall be recorded.  The eight cycles shall include four pre-trigger and four post-trigger cycles.  The waveform capture shall be configurable to trigger by manually over communications (when specified), by a overcurrent trip, by a protective relay trip (when specified), or by a current alarm.  Waveform data shalle be available in "comtrade" file format via serial communications or at a front port at the trip unit. ]

Specifier Note:  Include the following for Protective relay option.

#### [The trip unit shall include all of the following protective functions. It shall be possible to disable, by user programming, any combination of unwanted protective functions. Except for reverse power, relay settings shall be in 1 percent steps over indicated range. Each function shall have a time delay, adjustable in 1-second increments (1 to 15 seconds) and shall be able to be switched OFF.  If the manufacturer’s trip unit can not incorporate the specified functions, separate device(s) with equal functions shall be provided for each breaker.

##### Undervoltage, adj. pickup, 50 to 90 percent; 1% increment adj. delay, 1 to 15 seconds.

##### Overvoltage, adj. pickup, 110 to 150 percent; 1% increment adj. delay, 1 to 15 seconds.

##### Voltage unbalance, adj. pickup, 10 to 50 percent; adj. delay, 1 to 15 seconds.

##### Current unbalance, adj. pickup, 10 to 50 percent;  1% increment adj. delay, 1 to 15 seconds.

##### Reverse power, selectable direction, adj. pickup, 10 KW to 990 KW; 10kW increment adj. delay, 1 to 15 seconds.]

### [Trip units for Molded Case Circuit Breakers

#### Main [and feeder] molded case circuit breakers shall be supplied with digital electronic trips [where indicated on drawings].  Furnish GE microEntelliGuard digital electronic trip units or equal that complies with all of the following.

#### The protective trip unit shall consist of a solid state, microprocessor based programmer; tripping means; current sensors; power supply and other devices as required for proper operation.

#### Long time and short time protective functions shall have true RMS sensing technology for harmonic rich currents including up to the 19th harmonic.

#### High contrast liquid crystal display (LCD) unit shall display settings, trip targets, and the specified metering displays.

#### Multi-button keypad to provide local setup and readout of all trip settings on the LCD.

#### An integral test jack for testing via a portable test set and connection to a battery source.

#### Noise immunity shall meet the requirements of IEEE C37.90.

#### Display trip targets for long time, short time, and ground fault, if included.

#### Visual illuminated indication of the trip unit (normal, pickup, trip, error).

#### The trip unit shall be provided with a 10 event trip history log.  Each trip event shall be recorded with type, phase and magnitude of fault that caused the trip

#### As a minimum, the trip unit shall have the following protective functions:

##### Current setting or long time pickup, adjustable from 100% of sensor to 20% or less of the sensor value. Trip unit may use trip rating plugs, or not.

##### Adjustable long time delay with typical inverse time characteristics.  In addition, a set of straight line fuse shaped (I4t) long time delay bands shall be provided to facilitate selectivity with downstream fuses.

##### Instantaneous pickup, with sufficient adjustability to ensure selective coordination with downstream branch devices up to the full short circuit current available at the motor control center. When require zone selective interlocking shall be provide to improve protection or selectivity.  If molded case circuit breakers cannot provide required selectivity, stored energy circuit breakers of sufficient size and rating, or Low Voltage Power Circuit Breakers (UL 1066) of sufficient size and rating shall be substituted to achieve required selective performance.

##### Short-time pickup and delay. Short time protection shall include at least two curve shapes; definite time and I2t shapes with adjustable pickup and adjustable delay bands.

##### [Adjustable ground fault pickup and delay.  Ground fault protection shall include at least three curve shapes; definite time, I2t and I4t shapes with adjustable pickup and adjustable delay bands.  [Where indicated on the drawings provide GF alarm only function which shall operate an output control contact]

#### Specifier Note:  Also known as a maintenance switch or alternate setting group. Called RELT by GE. In GE MCC it will be provided with a 3 position control switch that allows testing of the required control power and status indication and indicates trip unit protective status (positive feedback) via a contact closure provided by the trip unit.

##### Main circuit breaker trips 800A and above shall implement a maintenance switch function that allows an instantaneous protection setting, separately adjustable, to be set via an external signal to the circuit breaker trip.  The function shall be implemented such that it operates from a separately mounted three position switch. The switch positions shall be “Normal or Off” (maintenance instantaneous disabled), “Test” (used to test control power circuitry and signal wiring), and “ON” (which is used to enable the maintenance instantaneous protection). The switch shall include indicating light(s) to indicate that the test function is working properly and that the additional protection has been enabled at the trip unit (positive feedback). When the maintenance instantaneous protection is turned “off” the protection shall delay at least 15 seconds before it goes back to normal protection. If the trip unit or relay does not provide that delay a separate timing control shall be installed to provide at least a 15 second off delay for the maintenance switch function.

#### The trip unit shall display rms current, each phase, on the LCD.

#### Specifier Note:  Include the following for advanced metering options.

#### [The following monitored values shall also be displayed on the trip unit LCD:

##### Voltage, rms, line - to - line, or line - to - neutral;

##### Energy, KWH, total;

##### Demand KWH, over an adjustable time period of 5 to 60 minutes;

##### Peak demand, KW, user resettable;

##### Real power, KW, line - to - line, line - to - neutral;

##### Total (apparent) power, KVA, line - to - line, line - to - neutral.

##### Reactive Power, KVAR, line - to - line, line - to - neutral.

##### Power Factor (%)

##### Frequency (Hz)]

#### Trip unit shall be provided with serial communications using Modbus RTU protocol. Manufacturer’s literature shall provide full register map.

#### Trip unit shall provide waveform capture capability for fault events. Capture data shall include 4 cycles before and 4 cycles after the event. Data shall be provided in a Comtrade file format for use by power management system.

#### If a manufacturer’s trip unit can not incorporate the above specified metering functions, separate device(s) with equal function shall be provided for each breaker

#### Specifier Note:  Include the following for protective relays

#### [The following protective relay functions shall be provided. User shall be able to enable or disable each option as required by the coordination study. If the manufacturer’s trip unit cannot incorporate the specified functions, separate device(s) with equal function shall be provided for each breaker.

##### Undervoltage, adj. pickup, 50 to 90 percent; adj. delay, 1 to 15 seconds.

##### Overvoltage, adj. pickup, 110 to 150 percent; adj. delay, 1 to 15 seconds.

##### Voltage unbalance, adj. pickup, 10 to 50 percent; adj. delay, 1 to 15 seconds.

##### Current unbalance, adj. pickup, 10 to 50 percent; adj. delay, 1 to 15 seconds.

##### Reverse power, adj. pickup, 10 KW to 990 KW; adj. delay, 1 to 15 seconds.

##### Load alarm, adj. ON, 0.55 to 1.0 x Longtime pickup; adj. OFF, 0.5 to 0.95 x Longtime pickup.]]

### Communication Relays for Smart MCCs

#### [Solid-state, ambient compensated in operating range of 20…+60°C (-4…+140°F), self-powered, 50% phase imbalance, phase loss protection, selectable overload class (10, 15, 20, 30), 2.5-5% accuracy, 1%repeat accuracy, isolated 1NO and 1NC auxiliary contacts, with [Profibus] or [DeviceNet] or [Ground Fault] or [none] modules]

- Note to Specifier: This following reflects capabilities of the GE Multilin MM200 Relay for more information please see: https://www.gedigitalenergy.com/multilin/catalog/mm200.htm:

#### Motor management shall be provided using a relay with complete protection, metering, and monitoring functions. The relay may be applied on induction motors up to 690V AC, VT or directly connected @ 60 Hz from 0.5 to 1000 FLA in steps of 0.1.

#### The protection functions shall include selectable overcurrent Class 10, 15, 20, & 30, adjustable current unbalance, Zero Sequence ground fault if specified on drawings, fixed over/under-voltage, adjustable Stall & Jam, selectable Load & Power Loss, auxiliary sense failure, stop motor and record event upon failure of an auxiliary device to change state upon command.  Advanced thermal model (various standard overload curves, unbalance current biasing that accounts for negative-sequence heating, hot/cold biasing that accounts for normal temperature rise, available RTD biasing that accounts for the rapid heating that occurs during stall, acceleration and overload, cooling rate that accounts for heat dissipation, thermal protection reset that controls recovery from thermal trips and lockouts.

#### The relay shall be equipped with the following protection functions:

##### The relay shall detect ground faults or earth leakage currents as low as 0.50 A using a 50:0.025 Ground CT.

##### Use phase and unbalance current heating to calculate motor thermal capacity during starting and running states

##### Settable motor stopped and motor running cooling time constants

##### Ground Instantaneous overcurrent elements (50G)

##### Unbalance / single phase biasing (46)

##### Load-loss (undercurrent) (37)

##### Ground time overcurrent (51G)

##### Locked/stalled rotor, mechanical jam (51R)

##### Motor stall protection

##### The relay shall be equipped with an acceleration timer

##### The relay shall be equipped with a load increase alarm

##### The relay shall have a thermistor input.

##### The relays shall have internal Current Transformers (C.T.’s) rated and 1A/5A and shall be suitable for direct connection up to 5A FLA.

##### The relay power supply shall be rated at 24VDC or an AC power supply rated at 60 – 300VAC

##### The relays shall be capable of operating with 50Hz and 60 Hz systems

##### The relay shall have programmed starter logic and shall support the following starter types.  Full Voltage Non-Reversing (FVNR), Full Voltage Reversing (FVR), Two Speed, Inputs and Outputs shall be automatically assigned based on the starter type.

##### The relay shall be capable of being DIN rail mounted.

##### Digital Inputs

###### [The relay shall have two (2) Form A and one (1) Form C outputs.]

###### [The relay shall have seven (7) digital inputs rated at 24VDC.]

###### Or

###### [The relay shall have two (2) Form A and one (1) Form C outputs.]

###### [The relay shall have six (6) digital inputs rated at 65 to 300 VAC.]

##### The relay shall be suitable to operate in temperatures from –20 degrees Celsius to +60 degrees Celsius with up to 90% non-condensing humidity.

#### The relay shall provide complete monitoring and metering functions. These shall include:

##### Current: RMS Values of per Phase, Average Current, Ground Current, Motor Load, Current Unbalance, Thermal Capacity

##### The relay shall provide the following information:

###### Total number of trips

###### Overload trips

###### Mechanical jam trips

###### Undercurrent trips

###### Current Unbalance trips

###### Ground fault trips

###### Motor acceleration trips

##### The relay shall capture the number of motor starts and motor running hours.

##### The following learned data shall be provided:

###### Learned acceleration time

###### Learned starting current

###### Learned starting capacity

###### Learned average motor load

Specifier Note: the following meters represent the GE Multilin MM300 offering. For more information please see: https://www.gedigitalenergy.com/multilin/catalog/mm300.htm

#### Motor management shall be provided using a relay with complete protection, metering, and monitoring functions. The relay may be applied on induction motors from 110 to 690V AC, VT or directly connected @ 60 Hz from 0.5 to 1000 FLA in steps of 0.1.

#### The protection functions shall include selectable overcurrent Class 10, 15, 20, & 30, adjustable current unbalance, Zero Sequence ground fault if specified on drawings, fixed over/under-voltage, adjustable Stall & Jam, selectable Load & Power Loss, auxiliary sense failure, stop motor and record event upon failure of an auxiliary device to change state upon command.  Advanced thermal model (various standard overload curves, unbalance current biasing that accounts for negative-sequence heating, hot/cold biasing that accounts for normal temperature rise, available RTD biasing that accounts for the rapid heating that occurs during stall, acceleration and overload, cooling rate that accounts for heat dissipation, thermal protection reset that controls recovery from thermal trips and lockouts.

#### Ground faults or earth leakage currents as low as 0.50 A using a 50:0.025 Ground CT.

#### Use phase and unbalance current heating to calculate motor thermal capacity during starting and running states

#### Settable motor stopped and motor running cooling time constants

#### Ground Instantaneous overcurrent elements (50G)

#### Unbalance / single phase biasing (46)

#### Load-loss (undercurrent) (37)

#### Undervoltage, auxiliary input (27x)

#### Ground time overcurrent (51G)

#### Locked/stalled rotor, mechanical jam (51R)

#### Motor stall protection

#### Re-start blocking timer to be used as a start permissive to ensure the motor had slowed to a safe speed or to a complete stop, before it can be re-started again

#### Starts-per-hour (66)

#### Minimum-time-between-starts

#### The relay shall be available with a voltage input rated up to 690VAC direct connect.

#### Available protection with the voltage input shall include overvoltage (59), undervoltage (27), voltage phase reversal (47).

#### The relay shall be available with an Undervoltage Auto-restart function that will restart the motor after an undervoltage trip caused by a momentary loss of power.

#### Available 6 RTD inputs with associated over-temperature protection functions including alarm and trip settings, with corresponding settable time delays, and associated outputs.

#### Protection functions associated to Power

##### a thermistor input.

#### Monitoring and metering functions shall include:

##### Phase current, each phase and ground; average current; % current unbalance; voltage; power factor, three-phase power, elapsed motor hours.

##### Current: RMS Values of per Phase, Average Current, Ground Current, Motor Load, Current Unbalance, Unbalance Biased Motor Load, Ground, Differential Currents

##### Voltage: Phasors, RMS Values of Phase-Phase and Phase-Neutral, Average Voltage

##### Frequency

##### Temperature of each RTD Inputs

##### Power: Power Factor, Three phase Real (kw), Reactive (kvar), Apparent (kva) Power

##### Energy: Watt-hours, Var-hours

##### An event recorder with a record of the last 255 events, time tagged with a resolution of 10 ms.

##### The waveform capture feature is similar to a transient/fault recorder. The relay shall storage of up to 32 cycles of data, captured for Phase A, B, and C currents (Ia, Ib, and Ic), Ground currents (Ig), Phase A-N, B-N, and C-N voltages (Van, Vbn, and Vcn) for wye connections, Phase A-B and B-C (Vab and Vbc) for open-delta connections

##### Non-volatile memory that can store up to 10 trip events.

##### The relay shall keep count of number of trips by type

##### Number of motor starts or start attempts

##### Number of Emergency Restarts

##### Motor running hours

##### Motor stopped hours

#### Control functions shall include:

# The relay shall have programmed starter logic and shall support the following starter types.  Full Voltage Non-Reversing (FVNR), Full Voltage Reversing (FVR), Wye-Delta, Two Speed, Reduced Voltage Start, and Inverter Start. Inputs and Outputs shall be automatically assigned based on the starter type.

##### Four output contacts with NEMA C150 pilot duty ratings. Two NO contacts shall be used to control motor contactors, one form-C contact shall be used to annunciate ground fault status as shown on drawings, and one form-C contact shall be used for programmable fault status indications.

      - The relay shall have expandable IOs. At least two (2) Form A output relays and six (6) digital inputs.

##### Six digital inputs for the following: Run 1, Run 2, Stop, Trip, Operation Mode, Reset.

##### Power Loss auto restart.  Upon power loss, the relay will record a power loss fault as well as latest motor condition and parameter settings. The relay shall have the ability to restart after a 4 second or less power outage.

      - The relay shall have ten (10) process interlocks that are used to provide trip, stop, or alarm based on contact input.

#### The Motor Protective relay shall include the following user interfaces:

##### Front mounted LED’s indicators shall indicate module status, network status, overcurrent pickup, ground fault pickup and current unbalance pickup.

##### Dip-switch configuration for overload trip class (10, 15, 20, 30), DeviceNet MAC ID, and Baud Rate. Software shall not be required for configuring these values.

##### DeviceNet communications using a standard 5-pin sealed micro style (female) connector. Software configured (Windows based)

        - Software configured (Windows based)An RS232 port, using an RJ11, on relay shall be provided for PC or Display device to access the settings and following data:

##### Phase Currents

##### Average Phase Current

##### Line Voltage

##### KW

##### Power Factor

##### Elapse Time

##### Trip record of last 10 events

##### Address (MAC ID)

##### Trip Class

##### Baud rate

##### Programming and Display Unit (PDU)

###### PDU shall have capability to configure the relay, display faults and all monitored parameters.

###### PDU shall have a 4-line by 16 character LCD display and control keys.

###### LED indicators on the PDU shall indicate control power availability and fault status.

##### GE EnerVista compatible Windows® based PC software which enables setpoint programming, file storage, on-line help, and real time display of status and measured data. Or equivalent with capabilities as described in this specification.

### Miscellaneous Units:  The following units shall be included in the motor control center(s) as indicated on the drawings:

Specifier Note:  Motor control centers can include lighting and power transformers up to 37.5 kVA single phase or 45 kVA three phase.

#### [Lighting and Power transformers]

#### [Lighting panelboards, type AQ or AL for 240V applications and type AE for 480V applications.]

#### [Power factor correction capacitors].

#### Specifier Note: Please see http://www.geindustrial.com/products/starters/solid-state-reduced-voltage for more information on GE’s Reduced Voltage Solid State Starter

#### [Reduced Voltage Solid State]

#### Specifier Note: Please see http://www.geindustrial.com/products/drives/low-voltage-ac for more information on GE’s Variable Frequency Drives

#### [Variable Frequency Drives]

Specifier Note: Please see http://www.ge-ip.com/products/programmable-logic-controller/c552 and http://www.ge-ip.com/products/pac-programmable-controllers/c547 for more information on GE’s Programmable Logic Controllers and GE’s Programmable Automation Controllers

#### [Programmable Logic Controllers] or [Programmable Automation Controllers]

## FINISH

### The Motor Control Center steel parts shall be cleaned and sprayed in controlled cleaning solutions by a 7-stage spray washer. The operation shall produce an iron phosphate coating of a minimum of 150 milligrams per square foot to meet MIL Specification TT-C-490. The primed metal parts shall be electrostatically coated with powder paint consisting of 670-011 ANSI-61 Acrylic Paint (Light Gray) with a gloss of 60 plus or minus 5 and thickness of 2.5 mils. The paint finish shall withstand a minimum of 1000 hours salt spray test.

### Unpainted steel parts shall be zinc plated.

### Interior of units shall be painted white for better visibility.

## TESTING

### Electrical tests before shipment shall include:

### Power circuit phasing

### Control circuit wiring

### Instrument transformers

### Meters

### Device electrical operation

### AC Dielectric tests (per NEMA ICS 1-109-21) of:

### Power circuits

### Control circuits

# EXECUTION

## EXAMINATION

### The following procedures shall be performed by the Contractor.

#### Examine installation area to assure there is enough clearance to install MCC.

#### Check concrete pads for uniformity and level surface.

#### Verify that equipment is ready to install.

#### Verify field measurements are as [{shown on Drawings] [instructed by manufacturer}].

#### Verify that required utilities are available, in proper location and ready for use.

#### Beginning of installation means installer accepts conditions.

## INSTALLATION

Specifiers Note: Additional provisions and editing may be required for this part.

### Installation shall be performed by the Contractor.

#### Install per manufacturer's instructions.

#### Install required safety labels.

## FIELD QUALITY CONTROL	Specifiers Note: Additional provisions, editing or reference to appropriate contract clauses may be required for this part. Manufacturer’s testing agency recommended over independent third party agencies.

### To be provided by manufacturer’s field testing and commissioning organization

#### All control and power wiring shall be verified.

#### All devices shall be verified to be in proper working order, properly set for protection per the coordination study. Metering, diagnostic and control adjustments shall be made and documented as required for proper operation of the motor control centers.

#### All communicating devices shall be verified to be properly addressed and communicating within the networks they are intended to interact with.

#### Any adjustment of safety functions or devices such as maintenance switch settings, arc flash relays or other devices shall be made, controls verified and documented.

#### A commissioning report shall document that all the listed actions have been performed and verified.

## ADJUSTING	Specifiers Note: Additional provisions, editing or reference to appropriate contract clauses may be required for this part. Manufacturer’s testing agency recommended over independent third party agencies.

### To be provided by equipment manufacturer’s field service organization

#### All protective devices shall be set per the coordination study

#### All metering and diagnostic devices or functions shall be set to ensure they are in proper working order for the system within which they are being used.

#### Documentation shall be provided in the commissioning report that all adjustements have been made, including by whom, and when.

## CLEANING	Specifiers Note: Additional provisions, editing or reference to appropriate contract clauses may be required for this part.

### To be provided as required by installing contractor

#### Project to be left in proper working order by installing contractor per all other requirements in contract documents have been fulfilled, at the end of the project.

#### Project site and equipment shall be maintained clean during the project as appropriate for the construction stage.

#### Cleaning shall be provided at end of the project and during the project to ensure the site and equipment is available to personnel in a professional workmanship like manner at all times.

#### At no time during construction shall live conductors be left unterminated or unprotected.

END OF SECTION