# GENERAL

### The requirements of the Contract, Division 1, and Division 16 apply to work in this Section.

## SECTION INCLUDES

### Lighting Control Panelboards/systems.

## RELATED SECTIONS

### 16479, Transient Voltage Surge Suppression

## REFERENCES

### The lighting panelboards and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/NEMA KS 1, Enclosed and Miscellaneous Distribution Equipment Switches (600 Volts)

### ANSI/NEMA PB 1, Panelboards

### ANSI/NFPA 70, National Electrical Code

### Federal Specification W-C-375, Rev. B, Amend. 1, Circuit Breakers, Molded Case; Branch Circuit and Service

### Federal Specification W-P 115, Rev. C, Panel, Power Distribution

### NEMA AB 1, Molded Case Circuit Breakers and Molded Case Switches

### NEMA PB 1.1, General Instructions for Proper Installation, Operation and Maintenance of Panelboards Rated 600 Volts or Less

### UL 489, Molded-Case Circuit Breakers and Circuit-Breaker Enclosures

### UL 50, Enclosures for Electrical Equipment

### UL 67, Panelboards

### UL 916, Energy Management Equipment

### UL 943, Ground-Fault Circuit-Interrupters

### FCC Part 15, Subpart J for Class A applications

## DEFINITIONS

### Overcurrent Protective Device:  A circuit breaker pole or single fuse. Example: a 2-pole device is considered 2 protective devices.

## SYSTEM DESCRIPTION

### Short circuit rating of panelboards shall be the interrupting rating of lowest rated device in the panel or applicable UL series rating for proper main and branch device combinations.

### The lighting control panelboards shall have an internal or external controller that provides on/off control of lighting circuits and have network communications capability.

### Panelboards shall have a maximum of 42 branch protective devices per panel. For more than 42 devices, multiple panelboards shall be provided.

### Protective devices shall be motor driven molded case circuit breakers; conventional molded case breakers can be mounted for non-controllable circuits.

### Panelboards shall have 16 programmable inputs per panel.  Additional inputs up to 64 shall be provided by adding accessory switch input modules.

### Low Voltage switches shall be provided for remote lighting control.  In addition, motion sensors shall be provided for automatic on/off control based on occupancy.  Photocell sensors shall be provided for daylight harvesting purposes.

## SUBMITTALS

### Manufacturer shall provide copies of following documents to owner for review and evaluation in accordance with general requirements of Division 1 and Division 16:

#### Product Data on specified product.

#### Shop Drawings on specified product.

#### Certified trip curves for each specified product.

#### One-line Diagram of recommended system configuration.

#### Typical Wiring Diagrams for specified product.

## PROJECT RECORD DOCUMENTS

### Maintain an up-to-date set of Contract documents. Note any and all revisions and deviations that are made during the course of the project.

## OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division 1 and Division 16.

### Submit operation and maintenance data based on factory and field testing, operation and maintenance of specified product.

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of lighting and appliance panelboards and lighting control equipment for not less than 5 years.

### Lighting and appliance panelboards shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.03 of this specification.

### Installer has specialized in installing and programming lighting control panelboards with minimum 5 years documented experience.

### All components and assemblies are to be factory pre-tested.

### Factory Application Engineers shall be available for technical support.

## DELIVERY, STORAGE, AND HANDLING

### Deliver, store, protect, and handle products in accordance with recommended practices in manufacturer's Installation and Maintenance Manuals.

### Deliver each lighting panelboard in individual shipping cases for ease of handling. Each panelboard shall be wrapped for protection per manufacturer’s standard method, unless otherwise noted.

### Inspect and report concealed damage to carrier within specified time.

### Store in a clean, dry space. Maintain factory protection or cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic.

### Handle in accordance with NEMA and manufacturer's written instructions to avoid damaging equipment, installed devices, and finish.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow standard service conditions before, during and after panelboard installation.

### Lighting and appliance panelboards shall be located in well-ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between [0] and plus [40] degrees Celsius.

### Indoor locations shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 1 year from date of installation or 18 months from date of shipment, whichever occurs first.

## EXTRA MATERIALS

### Provide parts and/or spares as indicated in drawings.

## FIELD MEASUREMENTS

### Make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

# PRODUCTS

## MANUFACTURER

### General Electric Company products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## EQUIPMENT

### Furnish General Electric A-Series® Lighting Control Panelboards as indicated in drawings.

## LIGHTING CONTROL PANELBOARD

### The lighting control panelboard shall consist of a microprocessor-based internal or external modular controller with remote operated circuit breakers, bolted to a UL 67 listed panelboard interior, mounted within a UL 50 listed enclosure.

### Each lighting control panelboard shall have the following capabilities:

#### Sixteen (16) 2-wire or 3-wire digital maintained or momentary, and three (3) analog inputs.

#### Controller shall have a local control switch input that allows for override at the panel.

#### Any combination of inputs shall be programmable to any combination of outputs.  This shall be possible in either normally open or normally closed conditions.

#### Time of day scheduling with a real time astronomical clock in 12 or 24 hour format, and network time synchronization.

#### Sixteen (16) lighting groups/zones per panelboard, each group/zone with up to sixteen (16) on/off periods per day.

#### Ninety (90) special events/holiday schedules per year with 10 year programming of holidays, and daylight savings and leap year automatic  adjustments.

#### Operate breakers sequentially with the ability to program minimum or maximum on and off times.

#### Provide breaker open/closed status feedback to controller.  Record breaker burn (On-time) hours.  Maintain timestamp of each change of state.

#### Controller shall receive power from panelboard bus, such that all breaker spaces are available for branch circuit distribution.

#### Controller shall be networkable, and communicate peer-to-peer via standard open protocols of BACnet, Modbus RTU, and Modbus TCP.

#### Breakers from multiple panels shall have the ability to be grouped together into the same zone control scenarios.

#### Remote inputs shall be supported from any combination of handheld programmers, local PCs, network PCs, or other network devices such as other BACnet controllers.

#### Controller shall have RS232, RS485 [and Ethernet] ports for networking and programming.

#### Controller shall have self-diagnostics and allow upgrades to be installed over the network.

#### Controller shall have a non-volatile memory to retain all setup and program configuration.  Controller shall have flash memory for firmware upgrade, and battery back up sufficient for 30 days; and include power failure recovery.

#### Controller shall be accessible without removing the deadfront.

#### Controller shall support load priority management to enable the user to set load shed levels on each motor operated breaker.

#### The controller shall have an Autoflip feature that allows the user to automatically rotate the breaker mapping by 180 Degrees without re-programming or re-wiring.

#### Controller shall have a programmable flick warn feature for providing occupant warning of an upcoming off command.

#### Each controller shall operate on a peer to peer network.

#### Motor operated breakers shall have an Open/Closed status flag: White for Closed and Green for Open.

#### Breakers shall be rated for 50,000 open-close-open operations.

#### [Controller shall have daylight optimization module input to perform daylight harvesting by measuring the amount of available light and providing a control signal to a dimming mechanism to maintain a preset lighting level.]

### [Configuration Software

#### Software shall be designed specifically for the lighting control system, support system configuration, and run in a Windows environment.

#### For basic setup and control, the software shall serve as a configuration and diagnostic utility.  Basic features shall include support for configuring inputs, zones, breaker operations, and time schedules.  Software shall monitor breaker status, and status of the system.  Software shall be able to establish connections to the system through a controller front port, RS232 port, RS485 port[, and Ethernet port].

#### Controller shall have the capability to calculate track and report number of burn hours by individual circuit.

#### Controller shall report an alarm condition.]

## COMPONENTS/CONSTRUCTION

### Refer to Drawings for: actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; and other required details.

### Ratings

#### The panelboard shall be rated for [208Y/120V][480Y/277V] AC with a continuous current rating of up to 400A for main breaker or main lugs.  Minimum short circuit current rating shall be [65KA at 208Y/120V] [14KA at 480Y/277V].  Panelboard shall be [series][fully] rated to meet the required short circuit current rating specified on the contract drawings.

### Enclosure

#### Enclosure shall be NEMA [1][12][3R][4X].

#### Boxes shall be a nominal 20 inches wide and 6 inches deep with wire bending space per National Electric Code.

#### Fronts shall be reinforced steel with concealed hinges and concealed trim adjusting screws. Trim clamps are unacceptable.

#### All door locks shall be [Corbin][Yale] with retractable latches. All door locks shall be keyed for a single key.

#### All panelboard series ratings shall be prominently displayed on dead front shield.

#### Interiors shall permit top or bottom incoming cables.

#### [Metal directory card holders shall be permanently mounted on front door.]

### Bus bars

#### Bus bars shall be phase sequenced, fully insulated and supported by high impact Noryl (or equal) interior base assemblies.

#### Bus bars shall be fabricated using [aluminum (standard)] [copper].

##### Aluminum bus bars shall have sufficient cross sectional area [to meet UL 67 temperature rise requirements through actual tests] [to provide a current density of [750A] [600A] per square inch].

##### Copper bus bars shall have sufficient cross sectional area [to meet UL 67 temperature rise requirements through actual tests] [to provide a current density of [1000A] [800A] per square inch].

#### Bus bars shall be mechanically supported by zinc finished galvanneal steel frames to prevent vibration and damage from short circuits.

#### Terminations shall be UL tested and listed and suitable for UL [copper] [aluminum] wire.

#### Provide [1] continuous bus bar per phase. Each bus bar shall have sequentially phased branch circuit connectors for bolt-on branch circuit breakers. Bus bars shall be rated as indicated in drawings.

#### Split solid neutral bus shall be plated and located in main compartment for all incoming neutral cables to be same length.

#### [Two hundred percent (200%) rated neutral shall be provided on 208Y/120V panels where indicated on schedules or contract drawings.]

#### Lugs shall be rated for 75 Deg.C terminations.

#### Main lugs for copper conductors shall be [bolted] [compression] lugs. Lugs for aluminum conductors shall be compression lugs.

#### Lug bodies shall bolt in place.

### Circuit Breakers

#### Molded case circuit breakers shall be bolt-on devices for both 208Y/120V panels and 480Y/277V panels.

#### All circuit breakers shall have thermal and magnetic trip elements in each pole.

#### 2-pole breakers shall have internal common trip crossbars for simultaneous tripping of each pole.

#### Circuit breakers shall not be restricted to any mounting location due to physical size.

#### All motor operated branch breakers 15 to 30 amperes shall be able to be mounted in any panel position for twin or double mounting without space penalty. Sum of ratings for 2 such double branch breakers mounted opposite each other, shall not exceed 150 amperes.

#### Sub-feed circuit breakers shall be horizontally mounted.

#### Branch breaker panelboard connections shall be copper to copper.

#### All panelboard terminations shall be rated as indicated in drawings.

#### All breakers shall have an over center mechanism and be quick make and quick break.

#### All breakers shall have handle trip indication and a trip indicator in window of circuit breaker housing.

#### Breaker handle and faceplate shall indicate rated ampacity.

#### Circuit breaker escutcheon shall have standard ON/OFF markings.

#### Main breaker shall be UL listed for use with: Shunt, Under Voltage, and Ground Fault Shunt Trips; Auxiliary and Alarm Switches; and Mechanical Lug Kits.

## FINISH

### Boxes shall be corrosion resistant, zinc finish galvanneal.

### Fronts shall be powder finish painted ANSI 61 gray.

# EXECUTION

## EXAMINATION

### Verify that A-Series® panelboards are ready to install.

### Verify field measurements are as [shown on Drawings] [instructed by manufacturer].

### Verify that required utilities are available, in proper location and ready for use.

### Beginning of installation means installer accepts conditions.

## INSTALLATION

### Install per manufacturer's instructions.

### Install required safety labels.

### Install control wiring insulation tubing per NEC 725.55.

## FIELD QUALITY CONTROL

### Inspect installed panelboards for anchoring, alignment, grounding and physical damage.

### Check tightness of all accessible mechanical and electrical connections with calibrated torque wrench. Minimum acceptable values are specified in manufacturer's instructions.

## ADJUSTING/CLEANING

### Adjust all [circuit breakers] [,] [access doors] [,] [operating handles] for free [mechanical] [and / or] [electrical] operation as described in manufacturer's instructions.

### Clean interiors of panels to remove construction debris, dirt, shipping materials.

### Repaint scratched or marred exterior surfaces to match original finish.

### END OF SECTION