# GENERAL

## SECTION INCLUDES

### Low voltage power panelboards

## RELATED SECTIONS

### [16479] [26 43 13], Transient Voltage Surge Suppression

## REFERENCES

### The low voltage power panelboards and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

### ANSI/NEMA PB 1, Panelboards

### ANSI/NFPA 70, National Electrical Code

### Federal Specification W-C-375, Rev. B, Amend. 1, Circuit Breakers, Molded Case; Branch Circuit and Service

### Federal Specification W-P 115, Rev. C, Panel, Power Distribution

### Federal Specification W-S-865 - Heavy Duty Switches

### UL 489, Molded-Case Circuit Breakers and Circuit-Breaker Enclosures

### UL 50, Enclosures for Electrical Equipment

### UL 67, Panelboards

### UL 98, Enclosed and Dead Front Switches

## DEFINITIONS

### Overcurrent Protective Device - Single pole circuit breaker. Example: A 2-pole device is considered 2 protective devices.

## SYSTEM DESCRIPTION

### Equipment shall be [indoor] [outdoor] deadfront power panelboards for molded-case circuit breakers.

### Panelboards shall meet service entrance requirements when specified.

### Panelboards shall have integrated short circuit rating. Fully rated panel rating is that of lowest rated device in panelboard. Series rating are for the UL tested main-branch combination.

## SUBMITTALS

### Manufacturer shall provide copies of following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26]:

### Product Data on specified product;

### Shop Drawings on specified product;

### Trip curves for each specified product;

## INSTALLATION, OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division [1] [01] and Division [16] [26].

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of low voltage power panelboards for [25] years.

### Low voltage power panelboards shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.03 of this specification.

### Power panelboards shall be qualified for use in seismic areas as follows:

#### High seismic loading as defined in IEEE Std 693-1997, with 2.0 amplification factor .

#### IBC-2006, Sds = 1.63g, Ss = 240%, Ip = 1.5, for all z/h greater than 0 and Sds = 2.0g, Ss = 300%, Ip = 1.5, for z/h equal to 0 in accordance with ICC-ES-AC156.

#### Seismic compliance shall be qualified only through shake table testing.  Compliance by calculation is not acceptable.

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall deliver, store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Ship each low voltage power panelboard section in individual shipping splits for ease of handling. Each panelboard section shall be mounted on shipping skids and wrapped for protection.

### Contractor shall inspect and report concealed damage to carrier within specified time.

### Contractor shall store in a clean, dry space. Maintain factory protection or cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic.

### Contractor shall handle in accordance with manufacturer's written instructions to avoid damaging equipment, installed devices, and finish.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after panelboard installation.

### Low voltage power panelboards shall be located in well-ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus [30] and plus [25] degrees C. Indoor locations shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 1 year from date of installation or 18 months from date of purchase, whichever occurs first.

## FIELD MEASUREMENTS

### Contractor shall make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

# PRODUCTS

## MANUFACTURER

### General Electric Company products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## MANUFACTURED ASSEMBLIES

### Furnish Low Voltage Power Panelboards (or equal) as indicated in drawings.

## COMPONENTS

### Refer to Drawings for: actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; and other required details.

### Enclosures

#### Panel box shall be galvaneeled code gauge sheet steel with removable end walls.

#### Enclosures shall be surface mounted.

#### Enclosures shall be NEMA [1] [3R] [12] [as indicated on drawings].

#### Fronts

#### Provide a four piece front to cover wiring gutter and wiring access areas. [Provide a lockable hinged door] with semi-concealed hinges to cover access to circuit breakers.

#### [Hinged door fronts, when specified, shall be provided with (select one of the following three options) ] [a lockable inner door with leaf hinges.] [door-in-door.] [a front-hinged to box.] An inner door shall cover the circuit protective devices and shall be able to be locked.

#### [Door locks shall be] [GE Valox style] [Yale #511] [National, flush lift latch] [3 point latch].

### Interiors

#### Panelboard interior shall be designed and assembled such that circuit protective devices shall be solidly connected to the distribution panel vertical bus. The bus bars shall be attached to the feeder device by bolts and to the vertical bus by bolts and anti-turn methods.

#### Circuit breaker connectors shall be designed so that circuit breakers may be removed without disturbing adjacent devices.

#### Panelboards shall be rated as indicated in drawings. Main devices shall have maximum rating of 1200 amperes.

#### Panelboards shall have three vertically aligned bus bars.

#### Bus bars shall be [aluminum] [copper]. The bus bars shall have sufficient cross sectional area to meet UL 67 temperature rise requirements through actual tests. The bus bars shall be [standard density rated for 1000 amperes per square inch copper] [standard density rated for 750 amperes per square inch aluminum] [reduced density rated for 800 amperes per square inch copper] [reduced density rated for 600 amperes per square inch aluminum].

#### Bus bars shall be phase-sequenced and rigidly supported by high impact resistant, insulated bus supporting assemblies to prevent vibration or short circuit mechanical damage.

#### Neutral bus shall be [fully rated] [200 percent rated] where indicated on the drawings.

#### All solderless terminations shall be suitable for [copper] [aluminum] UL listed wire or cable and shall be tested and listed in conjunction with appropriate UL standards. Terminations shall be rated for use with conductor ampacity as assigned in the NEC 75 degree C table.

#### Ground wire terminations shall be provided as an optional kit for installation by panelboard installer without voiding UL label.

### Main and Branch Devices

#### Circuit breakers

##### Main and branch circuit breakers shall be quick-make, quick break, and trip indicating, GE Type low voltage molded-case (or equal).

##### Circuit breaker case shall have ON/OFF and International I/O position indicators.

##### Breaker faceplate shall list current rating, UL and IEC certification standards, and AIC ratings.

##### Circuit breakers shall be factory sealed and shall be date coded on breaker case.

##### Breakers shall be UL listed for reverse connection without restrictive line or load markings. Circuit breakers shall be able to mount in any operating position.

##### 3-pole breakers with ampere ratings greater than [150] ampere shall have interchangeable rating plugs.

##### All circuit protective devices shall have the following minimum symmetrical current interrupting capacity [18kA] [25kA] [35kA] [50kA] [65kA] [100kA]. Interrupting rating of breakers shall not be less than maximum short circuit current available at incoming line terminals as shown on plans.

##### Breakers shall have UL listed series ratings, if specified in drawings.

##### [Main circuit breaker frame sizes 400 –1200A shall be 100% current rated.]

#### Panelboard series-connected ratings shall be attached to the panelboard enclosure.

### [Digital Electronic Trip Unit for Molded Case Circuit Breakers

#### [Each distribution main circuit breaker with a frame size 400 amps and larger shall have digital electronic trip units as described below. ] [Where indicated on drawings, distribution panel circuit breakers with a frame size 400 amps and larger shall have digital electronic trip units as described below.]

#### Furnish GE microEntelliGuard digital electronic trip units or equal that complies with all of the following.

#### The protective trip unit shall consist of a solid state, microprocessor based programmer; tripping means; current sensors; power supply and other devices as required for proper operation.

#### Long time and short time protective functions shall have true RMS sensing technology for harmonic rich currents including up to the 19th harmonic.

#### High contrast liquid crystal display (LCD) unit shall display settings, trip targets, and the specified metering displays.

#### Multi-button keypad to provide local setup and readout of all trip settings on the LCD.

#### UL Listed interchangeable rating plug. It shall not be necessary to remove the trip unit to change the rating plug.  Rating plugs shall be available in sizes from 40% to 100% of the breaker sensor rating

#### An integral test jack for testing via a portable test set and connection to a battery source.

#### Noise immunity shall meet the requirements of IEEE C37.90.

#### Display trip targets for long time, short time, and ground fault, if included.

#### Visual illuminated indication of the trip unit (normal, pickup, trip, error).

#### The trip unit shall display rms current, each phase, on the LCD.

#### The trip unit shall be provided with a 10 event trip history log.  Each trip event shall be recorded with type, phase and magnitude of fault that caused the trip

#### As a minimum, the trip unit shall have the following protective functions:

##### Current setting or long time pickup, adjustable from 50% to 100% of the rating plug value.

##### Adjustable long time delay with typical inverse time characteristics (minimum of 10 bands).  In addition, a set of straight line fuse shaped long time delay bands shall be provided to facilitate selectivity with downstream fuses (minimum 7 bands).

##### Instantaneous pickup, adjustable from 2.0 to 10 times the rating plug in 0.5 increments

##### Short time pickup and delay. Short time pickup shall be adjustable from 1.5 to 9 times the long time pickup setting in 0.5 increments with an OFF option.  Provide minimum of 12 short time delay bands with three selectable I2t bands.

#### The trip unit unit on main breakers shall have the following additional protective functions:

##### [Adjustable ground fault pickup and delay.  Ground fault pickup shall be adjustable from 0.4 to 1.0 times the breaker sensor rating.  Provide a minimum of 15 ground fault delay bands with three selectable I2t bands.]  [Where indicated on the drawings provide GF alarm only function which shall operate an output control contact]

### SPECIFIER NOTE:  ZSI IMPLEMENTATION REQUIRES AT LEAST TWO LEVELS OF CIRCUIT BREAKERS THAT HAVE ZSI CAPABILITY. THE DOWNSTREAM BREAKER THAT SENDS THE SIGNAL AND THE UPSTREAM BREAKER THAT RECEIVES IT AND ADJUSTS ITS PROTECTION TIMING ACCORDINGLY.  GE SPECTRA MICROENTELLIGUARD G AND K FRAME CBS ARE ABLE TO PROVIDE ZSI FOR THE INSTANTANEOUS FUNCTION. INSTANTANEOUS ZSI ENABLES SELECTIVITY BETWEEN THESE MOLDED CASE CIRCUIT BREAKERS AND SIMILARLY EQUIPPED ENTELLIGUARD G, OR WAVEPRO CIRCUIT BREAKERS UP TO THE FULL SHORT CIRCUIT RATING OR WITHSTAND RATING OF THE LINE SIDE DEVICE.

##### [Zone Selective Interlocking for Short Time and Ground Fault, and interlocked to supply-side overcurrent devices.] [Zone Selective Interlocking for Short Time, Ground Fault and Instantaneous protection, and interlocked to supply-side overcurrent devices.]

### SPECIFIER NOTE:  ALSO KNOWN AS A MAINTENANCE SWITCH OR ALTERNATE SETTING GROUP. CALLED A RELT SETTING IN GE LITERATURE. IN GE SWITCHBOARDS IT WILL BE PROVIDED WITH A 3-POSITION SWITCH THAT ALLOWS TESTING OF CONTROL POWER AND INDICATES TRIP PROTECTIVE STATUS VIA A CONTACT CLOSURE PROVIDED BY THE TRIP UNIT.

##### [Reduced Energy Let-Through (RELT) Instantaneous trip.  When specified this feature shall be provided to provide a temporary setting for the instantaneous trip setting of the breaker.  Setting shall be adjustable down to 1.5X of the rating plug and shall be enabled through a switch mounted on front of the switchboard.  The switch shall be combined with an indicating light that positively indicates that the RELT is enabled or disabled.]

## [POWER METERING

### Provide a digital electronic power meter with the power panel.  Meter shall monitor the incoming line.  Meter shall be a General Electric model [EPM6000] [PQM] or approved equal that satisfies all the following requirements.

SPECIFIER NOTE:  INSERT THE FOLLOWING FOR THE EPM6000 METER

### The meter shall be UL listed and CE marked.

### Power meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems.

#### Meter shall support 3 element wye, 2.5 element wye, 2 element delta, 4 wire delta systems.

#### The meter shall accept universal voltage input.

#### Surge withstand shall conform to IEEE C37.90.1

#### The meter shall be user programmable for voltage range to any PT ratio.

#### Meter shall accept a burden of up to .36VA per phase, Max at 600V, 0.014VA at 120 Volts.

#### The meter shall accept a voltage input range of up to 416 Volts Line to Neutral, and a range of up to 721 Volts Line to Line.

#### Meter shall accept a current reading of up to 11 amps continuous.

### Power meter shall use a dual input method for current inputs.  Method one shall allow the CT to pass directly through the meter without any physical termination on the meter, ensuring the meter cannot be a point of failure on the CT circuit.  The second method shall provide additional termination pass-through bars, allowing the CT leads to be terminated on the meter.  The meter must support both termination methods.

#### Fault Current Withstand shall be 100 Amps for 10 seconds, 300 Amps for 3 seconds, and 500 Amps for 1 second.

#### Meter shall be programmable for current to any CT ratio.  DIP switches or other fixed ratios shall not be acceptable

#### Meter shall accept burden of 0.005VA per phase, Max at 11 Amps.

#### Meter shall begin reading at a 5mA pickup current.

#### Pass through wire gauge dimension of 0.177” / 4.5 mm shall be available.

#### All inputs and outputs shall be galvanically isolated to 2500 Volts AC.

#### The meter shall accept current inputs of class 10: (0 to 11) A, 5 Amp Nominal, and class 2 (0 to 2) A, 1A Nominal Secondary.

### The meter shall have an accuracy of +/- 0.1% or better for volts and amps, and 0.2% for power and energy functions.  The meter shall meet the accuracy requirements of IEC687 (class 0.2%) and ANSI C12.201(Class 0.2%).

#### The meter shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral.

#### The meter shall provide sampling at 400+ samples per cycle on all channels measured readings simultaneously.

#### The meter shall utilize 24 bit Analog to Digital conversion.

### The meter shall include a three line, bright red, .56” LED display.

#### The meter shall fit in both DIN 92mm and ANSI C39.1 Round cut-outs.

#### The meter must display a % of Load Bar on the front panel to provide an analog feel.  The % Load bar shall have not less than 10 segments.

### Power meter shall include virtual measurement upgrade packs, which shall allow user to future upgrade in the field without removing installed meter.

#### These virtual upgrade packs must be able to be updated without physically removing the installed meter.

#### Meter shall be a traceable revenue meter, which shall contain a utility grade test pulse allowing power providers to verify and confirm that the meter is performing to its rated accuracy.

### The meter shall include 2 independent communications ports, the one in the back and one at face plate, with advanced features.

#### One port shall provide RS485 open communication protocol speaking Modbus ASCII/RTU through back plate.

#### Baud rates shall be from 9600 baud to 57,600 baud.

#### The meter shall provide an optical IrDA port (through faceplate), as the second communication port, which shall allow the unit to be set up and programmed using a remote laptop without need for a communication cable.

#### Meter shall have 8 Bit, No parity.

### The meter shall provide user configured fixed window or rolling window demand.  This shall allow user to set up the particular utility demand profile.

#### Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features.

#### All other parameters shall offer max and min capability over the user selectable averaging period.

#### Voltage shall provide an instantaneous max and min reading displaying the highest surge and lowest sag seen by the meter.

### The meter shall support power supply of 90 to 265 Volts AC and 100 to 370 Volts DC.  Universal AC/DC Supply shall be available.

#### Meter power supply shall accept burden of 10VA max.

#### Meter shall provide upgrade rate of 100msec for Watts, Var and VA.  All other parameters shall be 1 second.

### The meter shall have a standard 1-year warranty.

### SPECIFIER NOTE:  INSERT THE FOLLOWING FOR THE PQM METER

### Metering shall include A, V, W, Wh, Wcost, var, varh, VA, VAh, Hz, and PF in True RMS or displacement (fundamental) quantities.

### Power analysis features shall include an event recorder, waveform capture, trace memory, harmonic spectrum display (through the 62nd harmonic with total harmonic distortion) and a data logger function. All analysis data shall be non-volatile.

### Current inputs shall be via 1 amp or 5 amp CTs and no VTs shall be required for voltages up to 600V.

### Local user interface shall include a keypad and display for entering all setpoints and reading all measured values, and LED indicators for output relays, communication status and alarm status.

### An RS232 computer interface port shall be located on the front panel. Two RS485 and one RS232 communication ports shall be provided for simultaneous access using ModBus® RTU protocol. Any communication port shall be programmable for access using DNP 3.0 Level 2 protocol. Windows® based software shall be provided to enable setpoint programming.

## ACCESSORIES

### [Dual] [Through-feed] lugs

### [Padlocks]

### Grounding bars. (Neutral bus shall have grounding lug for Service Entrance applications.)

### [Exterior mounted equipment label]

### [Furnish nameplates for each device as indicated in drawings. Color schemes shall be as indicated on drawings.]

### [Provide a TVSS as specified in Section [16479] [26 43 13]]

## FINISH

### Standard panelboard boxes shall be galvanealed (zinc finished) or galvanized.

### Fronts shall be coated with phosphatized rust inhibitor and finish coated with ANSI 61 light gray baked on powder coat.

### Screw fasteners shall be zinc coated to retard corrosion.

# EXECUTION

## EXAMINATION

### The following procedure shall be performed by the contractor.

### Verify that low voltage panelboards are ready to install.

### Verify field measurements are as shown on Drawings.

### Verify that required utilities are available, in proper location and ready for use.

### Beginning of installation means installer accepts conditions.

## LOCATION

## INSTALLATION

### Additional provisions and editing may be required for this part.

### Contractor shall install per manufacturer's instructions.

### Contractor shall install required safety labels.

## FIELD QUALITY CONTROL			N/A

## ADJUSTING					N/A

## CLEANING					N/A

END OF SECTION