# GENERAL

## SECTION INCLUDES

### Low Voltage, Front-Connected free standing switchboards with a circuit breaker for main with lugs and color coded quick connect receptacles for connection to temporary generator.

## REFERENCES

### The low voltage switchboards and protection devices in this specification are designed and manufactured according to latest revision of the following standards (unless otherwise noted).

#### ANSI 61

#### ANSI/NEMA PB 2, Deadfront Distribution Switchboards

#### ANSI/NEMA PB 2.1, General Instructions for Proper Handling, Installation, Operation, and Maintenance of Deadfront Distribution Switchboards Rated 600 Volts or Less

#### ANSI/NFPA 70, National Electrical Code

#### NEMA AB 1, Molded Case Circuit Breakers and Molded Case Switches

#### UL 489, Molded Case Circuit Breakers

#### UL 891, Dead Front Switchboards

#### UL 1691, Single Pole Locking-Type Separable Connectors

## DEFINITIONS

### Front-Connected only shall be as defined by UL 891 standard which requires that all line and load connections for phase, neutral, and ground conductors can be made and maintained from the front of the switchboard without access to the rear.

## SYSTEM DESCRIPTION

### The power system feeding Switchboard (insert designation) is [208] [480] volts, [50] [60] Hertz, 3 phase, 4 wire, solidly grounded wye.

### Switchboard(s) shall have front connection with front and rear alignment for mounting against a wall for amperage ratings 800-4000A.

## SUBMITTALS

### Manufacturer shall provide [3] copies of the following documents to owner for review and evaluation in accordance with general requirements of Division [1] [01] and Division [16] [26]:

#### Product Data on specified product;

#### Shop Drawings on specified product;

## INSTALLATION, OPERATION AND MAINTENANCE DATA

### Manufacturer shall provide [3] copies of installation, operation and maintenance procedures to owner in accordance with general requirements of Division [1] [01] and Division [16] [26].

## QUALITY ASSURANCE (QUALIFICATIONS)

### Manufacturer shall have specialized in the manufacture and assembly of low voltage switchboards for 25 years.

### Low voltage switchboards shall be listed and/or classified by Underwriters Laboratories in accordance with standards listed in Article 1.03 of this specification.

### [Equipment shall be qualified for use in seismic areas as follows where required:]

#### High seismic loading as defined in IEEE Std 693-1997, with 1.33 amplification factor.

#### IBC-2009, Sds = 1.79g, Ss = 2.69g, Ip = 1.5, for all z/h equal to 1.0 and Sds = 2.90g, Ss = 4.35g, Ip = 1.5, for z/h equal to 0 in accordance with ICC-ES-AC156.

#### Seismic compliance shall be qualified only through shake table testing.  Compliance by calculation is not acceptable.

## DELIVERY, STORAGE, AND HANDLING

### Contractor shall store, protect, and handle products in accordance with recommended practices listed in manufacturer's Installation and Maintenance Manuals.

### Ship each switchboard section in individual shipping splits for ease of handling. Each section shall be mounted on shipping skids and wrapped for protection.

### Contractor shall inspect and report concealed damage to carrier within 48 hours.

### Contractor shall store in a clean, dry space. Cover with heavy canvas or plastic to keep out dirt, water, construction debris, and traffic. Heat enclosures to prevent condensation.

### Contractor shall handle in accordance with manufacturer's recommendations to avoid damaging equipment, installed devices, and finish. Lift only by manufacturers recommended procedures.

## PROJECT CONDITIONS (SITE ENVIRONMENTAL CONDITIONS)

### Follow (standards) service conditions before, during and after switchboard installation.

### Low voltage switchboards shall be located in well - ventilated areas, free from excess humidity, dust and dirt and away from hazardous materials. Ambient temperature of area will be between minus 30 and plus 40 degrees C. Indoor locations shall be protected to prevent moisture from entering enclosure.

## WARRANTY

### Manufacturer warrants equipment to be free from defects in materials and workmanship for 1 year from date of installation or 18 months from date of purchase, whichever occurs first.

## FIELD MEASUREMENTS

### Contractor shall make all necessary field measurements to verify that equipment shall fit in allocated space in full compliance with minimum required clearances specified in National Electrical Code.

# PRODUCTS

## MANUFACTURER

### General Electric Company products have been used as the basis for design. Other manufacturers' products of equivalent quality, dimensions and operating features may be acceptable, at the Engineer's discretion, if they comply with all requirements specified or indicated in these Contract documents.

## EQUIPMENT

### Furnish GE Type Spectra GenTower Switchboards (or approved equal).

## COMPONENTS

### Refer to Contract Drawings for actual layout and location of equipment and components; current ratings of devices, bus bars, and components; voltage ratings of devices, components and assemblies; interrupting and withstand ratings of devices, buses, and components; and other required details.

### Standard Features

#### Switchboards shall be fully self-supporting structures with 90 inch tall vertical sections (excluding lifting eyes and pull boxes) bolted together to form required arrangement.

#### Switchboard frame shall be die formed, 12 gauge steel with reinforced corner gussets. Frame shall be rigidly bolted to support cover plates (code gauge steel), bus bars and installed devices during shipment and installation.

#### All sections may be rolled, moved or lifted into position. Switchboards shall be capable of being bolted directly to the floor without the use of floor sills.

#### All switchboard sections shall have open bottoms and removable top plate(s) to install conduit.

#### Front-Connected switchboard sections shall be front and rear aligned.

#### Switchboards shall be UL listed.

#### Switchboards shall be fully rated for the available short circuit rating up to an including 65kA at 480V.

#### All covers shall be fastened by hex head bolts.

#### Provide hinged doors over, individually mounted device compartments and quick connect compartments. All doors shall have concealed hinges and be fastened by hex head bolts.

#### Switchboard protective devices shall be furnished as listed on drawings and specified herein, including interconnections, instrumentation and control wiring. Switchboards and devices shall be rated for the voltage and frequency listed on the drawings.

#### Switchboard current ratings, including all devices, shall be based on a maximum ambient temperature of 40 degree C per UL Standard 891. With no derating required, temperature rise of switchboards and devices shall not exceed 65 degrees C in a 40 degree C ambient environment.

### Incoming Section

#### Incoming section shall be direct cable connection to main breaker

#### Furnish switchboard(s) arranged for [bottom] [top] entry of incoming cable.

#### Provide mechanical type lugs suitable for 350-600 kcmil in the quantity listed in the following table.  All lugs shall be tin-plated aluminum and UL listed for use with copper or aluminum cable.  Lugs shall be rated for 75 degree C. Cable.

Amperage       Phase    Neutral   Ground

800		5	5	5

1000		5	5	5

1200		5	5	5

1600		5	5	5

2000		6	6	6

2500		8	8	8

3000		9	9	9

4000		12	12	12

### Bus Bars

#### Bus bars shall be silver-plated copper. The bus bars shall have sufficient cross sectional area to meet UL 891 temperature rise requirements.  Phase and neutral bus ampacity shall be as shown on the plans. The neutral bus shall have the same ampacity as the phase bus.

#### Bus bars shall be mounted on high impact, non-tracking insulated supports. Joints in the vertical bus are not permitted.

#### Bus bars shall be braced to withstand mechanical forces exerted during short circuit conditions as indicated in drawings, but in no case less than 65KA RMS SYM.

#### Bus joints shall be bolted with high tensile steel Grade 5 bolts.

#### Ground Bus shall be sized to meet UL 891. Ground bus shall extend full length of switchboard.  Ground bus shall be copper

#### A-B-C bus arrangement (left to right, top to bottom, front to rear) shall be used throughout to assure convenient and safe testing and maintenance. Where special circuitry precludes this arrangement, bus bars shall be labeled.

#### The main incoming bus bars shall be rated for the main protection device frame size.

### Enclosure

#### Switchboard(s) shall be NEMA 3R non walk-in deadfront construction.

#### NEMA 3R construction shall be as listed below.

##### Consist of standard indoor cubicles with a front frame and roof assembly to provide a weather resistant structure. Screen protected vents. Roof, front doors and rear covers shall be galvanized before painting.

##### Front hinged doors with padlocking provision and wind stop. Bolted rear covers on front access versions.

##### Provide hinged cable entry door to allow access to the lugs or cam-type receptacles while maintaining NEMA 3R integrity.

### Main Devices

#### Main device shall be individually mounted, insulated case circuit breaker. Main breaker shall be provided with Key interlock provisions so that the -GenTower switchboard main can be interlocked with the normal switchboard main or emergency feeder breaker. Field coordination is required for key interlock.

#### Breakers shall be constructed of a high dielectric strength, glass reinforced insulating case. The interrupting mechanism shall be arc chutes. Steel vent grids shall be used to suppress arcs and cool vented gases. Interphase barriers shall to isolate completely each pole.

#### Breakers shall contain a true two-step stored energy operating mechanism which shall provide quick make, quick break operation with a maximum five cycle closing time. Breakers shall be trip free at all times. Common tripping of all poles shall be standard.

#### Stationary mounted Insulated Case circuit breakers up to 3000A shall be rated to carry 100 percent of their frame ampacity continuously, 4000A circuit breaker shall be draw-out rated to carry 100 percent of the frame ampacity

#### A charging handle, close push-button, open push-button, and Off/On/Charge indicator shall be located on the breaker escutcheon and shall be visible with the breaker compartment door closed.

#### Where indicated provide the following with the main device:

##### key interlock provisions – standard

##### bell alarm – standard

### Digital Electronic Trip Unit for Insulated Case Circuit Breakers

#### Each insulated case PowerBreak II breaker shall be equipped with a digital electronic trip unit. The trip unit shall provide protection from overloads, and short circuits and shall alarm ground faults. The protective trip unit shall consist of a solid state, microprocessor based programmer; tripping means; current sensors; and other devices as required for proper operation.  Furnish GE Entelliguard TU digital electronic trip units as specified below.

#### As a minimum, the trip unit shall have the following protective functions unless otherwise indicated on the drawings:

##### adjustable current setting or long time pickup;

##### adjustable long time delay (22 bands);

##### switchable, adjustable short time pickup and delay (11 bands) with 3 i2t selectable slopes;

##### adjustable instantaneous pickup;

##### Ground fault alarm only function with adjustable pickup and delay.

#### As a minimum, the trip unit shall include the following features:

##### Long time and short time protective functions, if provided, shall have true RMS sensing technology and thermal long time memory.

##### High contrast liquid crystal display (LCD) unit shall display settings, trip targets, and the specified metering displays.

##### Multi-button keypad to provide local setup and readout of all trip settings on the LCD.

##### UL Listed interchangeable rating plug. It shall not be necessary to remove the trip unit to change the rating plug.

##### A mechanism for sealing the rating plug and the trip unit.

##### Noise immunity shall meet the requirements of IEEE C37.90.2.

##### Display trip targets for long time, short time, and ground fault, if included.

##### The trip unit shall keep a log of the last ten events including overcurrent trips, protective relay trips.  The log shall store RMS currents, phase, type of trip, trip counter, time and date for each event.

##### Instantaneous trip shall utilize filtering which permits fully selective operation with downstream current limiting devices up to the short time rating of the circuit breaker, when the instantaneous pickup is set above the current limiting threshold.

#### The trip unit shall include the following metering functions, which shall be displayed on the LCD (if the manufacturers trip unit can not incorporate the specified functions, separate device(s) with equal function shall be provided for each breaker):

##### Current, RMS, each phase;

## GENERATOR WIRING TERMINATIONS

### The switchboard shall be provided with both cam-type receptacles and mechanical lugs for connection of the temporary generator.  Cable supports shall be provided in the generator termination compartment to tie the cables from the temporary generator

#### Cam-type receptacles

##### Receptacles shall be Hubbell type HBLFRSC rated for 400 amps for use with the HBL400M series of male cable plugs

##### Receptacles shall be accessible from the exterior of the switchboard through a hinged cover.

##### c.          Cam-type receptacles shall be provided for phase, neutral and ground conductors from the generator.  Receptacles shall be mounted on a color coded panel. Colors shall be Brown, Orange and Yellow for the phase conductors for 277/480V systems and shall be Black, Red and Blue for the phase conductors for 120/208V systems.  The neutral connections shall be white and the ground conductors green.

##### Cam-type receptacles shall be single pole with brass contact material and shall be UL listed for attachment plugs to UL 1691.

##### Quantity of receptacles shall be per the following table unless otherwise indicated on the drawings:

Amperage	Per Phase	Neutral		Ground

800		4		4		2

1000		4		4		2

1200		4		4		2

1600		4		4		2

2000		5		5		2

2500		7		7		2

3000		8		8		2

4000		10		10		2

#### Mechanical Lugs

##### Lugs shall be mechanical set screw type UL listed for the use of copper or aluminum conductors.  Lugs shall be rated for the connection of cables sized per the NEC at 75 deg. C.

##### Lugs shall be accessible from the exterior of the switchboard through a hinged cover.

##### Mechanical lugs shall be multi-range accepting cables sizes 350 kcmil thru 600 kcmil

##### Quantity of cable connections shall be per the following table for Front-Connected switchboards unless otherwise indicated on the drawings.

Amperage       Phase    Neutral   Ground

800		5	5	5

1000		5	5	5

1200		5	5	5

1600		5	5	5

2000		6	6	6

2500		8	8	8

3000		9	9	9

4000		12	12	12

## FINISH

### All steel surfaces shall be chemically cleaned prior to painting.

### Exterior paint color shall be ANSI 61 Light Gray over phosphate - type rust inhibitor.

## ACCESSORIES

### A master label shall be provided which describes the sequence of operation for the GenTower Switchboard.

## TESTING

### Verify proper operation of main breaker key interlock with building switchboard breaker when kirk lock is provided.

PART	3	EXECUTION

3.01	EXAMINATION

A. The following procedures shall be performed by the Contractor.

1. 	Examine installation area to assure there is enough clearance to install switchboard.

2. 	Check concrete pads for uniformity and level surface.

3. 	Verify that GenTower™ switchboards are ready to install.

4. 	Verify field measurements are as instructed by manufacture.

5. 	Verify that required utilities are available, in proper location and ready for use.

6. 	Beginning of installation means installer accepts conditions.

  - LOCATION

  - INSTALLATION

Additional provisions and editing may be required for this part.

A. 	Installation shall be performed by the Contractor.

#### Install per manufacturer's instructions.

2. 	Install required safety labels.

3.04	FIELD QUALITY CONTROL			N/A

3.05	ADJUSTING					N/A

  - CLEANING

- All interior and exterior surfaces shall be cleaned to remove any construction debris and dirt.

- Any scratches on the exterior shall be repaired.

END OF SECTION