# TENDER SPECIFICATIONS

Please rename the file before deliver to third party

(Remember to delete this window)

UNINTERRUPTIBLE POWER SUPPLY SYSTEMS

15 - 90 kW Modular UPS

Contents

1.	General	2

2.	Tender submission requirement	2

3.	Applicable standards	2

4.	Environmental conditions	3

5	System description	3

6	UPS design	4

7	Rectifier/charger	4

8	Inverter	5

9	Static bypass switch	5

10	Maintenance bypass	6

11	Battery / battery test	6

12	Interface	6

14	Parallel operation (if required)	7

15	Communication	8

16	Maintenance	8

17	Testing and commissioning	8

18	Options	8

19	Options for communications and monitoring	8

# General

1.1	This specification covers the design, supply, delivery, installation, testing and commissioning of a continuous duty, 3-phase, four-wire Uninterruptible Power Supply system complete with maintenance-free sealed battery.

The Uninterruptible Power Supply system, hereafter referred to as the UPS system, shall operate in conjunction with the existing power distribution system. In the event of a utility power supply loss it shall be able to supply independently clean and regulated uninterruptible power for computer equipment and other critical loads.

UPS topology shall be VFI-Voltage and Frequency Independent (according to IEC 62040-3), with automatic and maintenance bypass.

1.2	The UPS system  will have provisions for all necessary interface connections and ancillary items such that it can be easily and economically expanded at a future time with minimum disruption for increased capacity or to provide a fully redundant system.

  - The UPS system will be suitable for installation in compliance to National Electric Code NFPA 70.

# Tender submission requirement

  - The tender submission shall be in sufficient detail to show compliance to the specification and shall include a full set of descriptive and technical literature on the equipment and system proposed.

  - The following drawings and information are to be submitted with the proposal:

- Technical Data sheets

- Product description or detailed description of the UPS functionalities

- Product dimensions and weights

- Heat dissipation of each unit (PF=1)

- Functional relationship of various equipment

- Layout plan of control panel, alarm panel, mimic diagram.

# Applicable standards

The equipment herein described as well as all the individual materials it comprises  of will be  approved in compliance with the latest editions of the codes and applicable standards.

3.1	Safety standards

- NRTL listed according to UL 1778 5th edition – Standard for Safety Uninterruptible Power Supply

- NRTL listed according to CSA C22.2 No. 107.3 (Bi-national listing)

3.2	Electromagnetic compatibility (EMC)

- FCC Part 15 class A

3.3	Performance

- IEC 62040-3	Method of specifying the performance and test requirements.

# Environmental conditions

  - The UPS system shall be capable of withstanding any combination of the following environment conditions in which it must operate, without mechanical or electrical damage or degradation of operating characteristics:

- Ambient temperature:	0 to 40 degrees C (up to 50°C subjected to conditions)

- Relative Humidity:	up to 95% (non-condensing)

- Altitude	up to 1000 m a.s.l. without de-rating

  - Audible noise generated by the UPS system under any condition of normal operation shall not exceed the sound pressure level indicated in the “UPS technical data”, measured at a height of 1 metre and at 1 metre from the nearest UPS cabinet surface.

# System description

The UPS needs to have the capability to scale in power from 15 to 90kW.

The UPS will be sized to provide a minimum of ____ kVA/kW output ( 1 power factor rating)

The UPS will be able to supply at full rated (kVA) output for loads with power factor between 0.9 lagging and 0.9 leading.

The UPS will have an active power factor corrected IGBT converter/rectifier, capable of maintaining input power factor and input THDi within specifications without an additional input filter.

The UPS will be of transformer-free design, requiring no internal transformer in the main power path for the basic operation of the module.

The UPS will be able to operate in the following conditions:

  - On-line mode - During normal operation, the UPS system will be used to provide precise regulated and transient-free power to the computer equipment loads. The mains supply provides power to the rectifier/charger. The rectifier/charger will provide regulated DC power to support the inverter and simultaneously maintain the battery in a fully charged condition. The inverter will convert the DC power into regulated AC power for the load.

  - Battery mode - Upon failure of the mains supply, input power for the inverter will automatically be supplied from the directly connected battery. When the mains is restored or the standby generator set supply is ready, input power for the inverter and for recharging the battery will automatically be supplied from the rectifier/charger. If the input does not return, the UPS will automatically shut itself down in an orderly manner when the discharge limit of the battery is reached.

  - Modularity

The UPS must have modular architectures based on identical power modules which can be interchanged and connected in parallel, inside the UPS cabinet and hot swappable.

Power modules will be equipped with control and self diagnostic circuits, in order to easily individuate the faulty module and the specific failure inside it.

Power Modules must be lighter than 34 kg in order to be managed, in service and maintenance.

  - Internal Redundancy N+X

The  UPS  must  be  configurable  as  N+X  power  redundant  system,  with  modules  of 15kW.

This  kind  of  redundancy  must  guarantee  continuous  supply  and  protection  whenever  one  module  fails. Redundancy must be obtained through the load sharing technology.

  - Bypass mode - Upon the failure of static inverter, common among power modules, the no-break static transfer switch shall be activated automatically to isolate the faulty inverter and at the same time maintain a continuous supply to the system load. The automatic transfer mode shall also operate in the event of system overloading or if irregular or undesirable output for the load is detected. In this case, the system shall automatically return to the original mode of operation if the disturbance is cleared.

  - Manual Bypass mode - If the UPS system needs to be isolated for testing or removed from service for maintenance, the built-in maintenance bypass will transfer the loads from inverter to the mains without interruption and vice versa.

  - Power Conditioner mode - If the battery only must be taken out of service for maintenance, it will be disconnected from the rectifier/charger and inverter by means of an isolator. The UPS will continue to function and meet all the performance criteria specified herein except for the protection time requirement.

# UPS design

  - The equipment will be based of hot-swappable power modules of 15kW, with the capability to scale up in power up to 90kW within the same UPS frame.

  - The equipment will be realized in a solid self-support structure built with steel profiles and sheets.

  - Equipment will be accessible by front, through hinged doors with level lock and key.

  - Forced air-cooling will be provided to ensure that all components are operated within specifications with air entry in the front and exit on the rear (500mm required on the back).

  - Adequate space for termination will be provided for incoming and outgoing cables. The cables for interconnecting the UPS and battery cubicles shall be supplied from bottom or top side of the cabinet.

  - The equipment will be designed to allow easy access to its parts, testing points and terminals, so that verification and maintenance can be made without removing assembly parts.

5.3	UPS operations will be performed from the UPS front side.

5.4	All serviceable parts will be accessible from front and top of the UPS cabinet.

5.5	UPS must be designed with a centralized static bypass among power modules

5.7	UPS must be designed with common batteries among power modules

5.8	The equipment shall meet the requirements of protection class IP 20.

# Rectifier/charger

  - General - The rectifier/charger must consist of a IGBT fully controlled bridge, which converts the 3-phase utility voltage into a controlled and regulated DC voltage, in order to supply power to the inverter, and to simultaneously charge the battery.

  - Capacity - The rectifier/charger shall have sufficient capacity to support a fully loaded inverter and at the same time maintain the battery in a fully charged condition.

If the battery is fully discharged, the rectifier/charger shall recharge the battery to 80% of its fully charged condition preferably within 5 hours and at the same time supplying full load current to the system. Otherwise the UPS supplier shall specify the charging time required.

Each power module needs to deliver at least 9Amps for battery charging.

  - Power walk-in - The rectifier/charger must contain a timed walk-in circuit to limit the inrush current. The allowable initial inrush surge and the walk-in time should be adjustable and not exceed 15sec.

  - Sequential power walk-in - a sequential walk-in of every single rectifier/charger shall be automatically executed in case of the start up of a parallel system in order to limit the inrush current to the value of one single system.

  - Current and Voltage Limit - The rectifier/charger output current and voltage shall be limited to the battery supplier's recommendation.

# Inverter

  - General - The conversion of DC to AC must be accomplished by IGBT power transistors of the modules.

  - Failure of any components or power stage shall not interrupt the AC output instead it shall disconnect itself from the configuration while transferring the load to the static transfer switch and then activate an alarm.

  - Standard Control Battery - A control battery will be provided to furnish logic power which is independent of the inverter input or output power. The battery will provide the power required to operate the inverter logic until the load is transferred to the alternate source and the inverter is shut down in an orderly manner in the event of a failure of the logic solid- state power supply. In addition, the battery will provide power to the alarm system to maintain event records after a UPS failure and shutdown.

  - Output - The inverter output wave form will be controlled by microprocessor-based software (software generated sine wave) to ensure that the voltage THD is being limited especially for non-linear loads.

  - The wave form will be fed through a filter circuit and protected by fast fuses.

  - Neutral - The neutral of the inverter output will be electrically isolated from the grounded UPS system chassis.

  - The inverter will be able to handle short-circuit conditions without any damage.

  - Frequency Control - The output frequency of the inverter will be controlled by an oscillator that can be operated as a free running unit or in synchronised operation with a separate AC source or the future redundant inverter.

  - The Inverter shall be able to supply any type of loads, linear and non-linear.

  - The inverters shall be able to supply unity power factor load.

# Static bypass switch

  - The electronic bypass switch will consist of a pair of microprocessor controlled thyristors, used to provide an uninterruptible transfer of the load to the utility in case of overload or UPS malfunction conditions.

  - The electronic bypass switch will be able to operate in continuous way. In addition the static transfer switch will support 150% overload for 1 minute and a short circuit withstanding current of 65kA.

  - The electronic bypass switch will return the load automatically to the UPS when the malfunction or overload is cleared.

  - The number of automatic transfer/re-transfer from bypass to inverter when the status of the inverter logic signals an alarm conditions, will be selectable.

  - The electronic bypass switch will be able to be activated manually by a switch/push button to affect the transfer. The switching time from inverter to reserve and vice-versa shall be of no-break when synchronised.

  - According to standard IEC 62040-1 the electronic bypass will be equipped by back-feed protection contactor, to protect UPS input mains from dangerous (electroshock) operating conditions.
The contactor will be integral part of the UPS and installed inside UPS cabinet.

# Battery / battery test

  - A battery will provide the UPS system with a stored energy source.

The battery will be designed for standby power service.

  - Battery capacity Ah or W/cell will be sufficient to support the inverter for the required autonomy time, with the inverter operating at full rated load.

  - Tenderer will submit full technical data of the battery offered under the tender and will provide calculations to show the number of cells required and their capabilities which will match the load requirement and the charging characteristics of the UPS requirement being offered.

  - Battery design life is 10 years.

  - Tenderer will specify the recommended voltage per cell for float charging and recharging at 25 degrees C (or at recommended operating temperature) and the relative required recharging current.

  - The battery will be mounted on UPS matching cabinet: dimensions and weight characteristics will be part of the tender documentation.

  - The UPS system will be able to provide battery test in either manual or automatic ways (pre-selectable by date and time of day). 
If a battery fault is detected, an alarm to advise the operator about the faulty conditions will be performed.

# Interface

  - Color touch screen display on front side will be provided, showing the “single line” diagram by indicating symbols and showing main measurement of UPS input, output as well as battery.

- Critical measurement of input, output and battery included with mimic diagram

- Quick operational status

- Different access level for user and service

- Different mimic diagram based on configuration

- Metering screen by tabs

- Multilanguage communication interface

- 10 inches+ dimension

  - Events - as a minimum the following UPS status and event list, with relative data and time, shall be provided:

- Rectifier:	rectifier ON, rectifier OFF, mains rectifier OK

- Battery:	start battery test, end battery test, no conditions for battery test

- Inverter:	inverter ON, inverter OFF, inverter cannot be switched ON/OFF,

- Bypass:	mains bypass OK, bypass locked, bypass free, bypass power insufficient

- Load:	load on inverter, load on bypass, load-OFF, overload condition, multiple load transfer

  - Alarms - a common audible alarm and the indication on control panel shall be initiated when any of the following conditions are present:

- UPS:	load off for overload; battery low and over-temperature conditions; inverter and 	mains not synchronised; UPS overload.

- Rectifier:	mains out of tolerance; control logic failure.

- Battery:	low voltage; high voltage; earth fault; contactor closing or opening failure

- Inverter:	fuse failure; contactor closing or opening failure; voltage out of tolerance; output 	power insufficient; overload.

- Bypass:	mains out of tolerance; contactor closing or opening failure

- Load:	overload; load locked on inverter; load locked on bypass

The list of alarms, with relative data and time, shall be provided.

  - Measurements  - as a minimum the following measurements shall be provided:

- UPS:	inverter and mains synchronised/not synchronised, input circuit breakers open/closed, maintenance bypass ON/OFF,

- Rectifier:	input voltage, input frequency, number of rectifier mains failure

- Battery:	autonomy time, voltage, temperature, charge/discharge current in A

- Inverter:	output voltage, output frequency, inverter temperature, operating hours

- Bypass:	input voltage (Ph-N), input frequency, number of bypass mains failure

- Load:	load level in % (each phase), load current/phase in A, Load power in kVA/kW

  - The UPS, through the control panel, will be able to store up to 256 alarms or events with date and time.

  - Service diagnostic: UPS needs to have the capability to store waveform in case an event occurs; Service Team needs to have these data in order to evaluate what happens on the UPS without waiting for the next event.

# Parallel operation (if required)

  - The 90kW UPS system could be extended with more UPS in parallel to increase system reliability or to increase total power system.

  - The Parallel system shall be capable to reach up to 270kW with N+X redundancy.

  - The transformation of the UPS from single to parallel shall be realized in easy way, without any main modification on the existing UPS components layout.

  - Parallel UPS shall have same characteristics and performances as for UPS in single configurations (efficiency, dynamic characteristics, output voltage distortion, etc).

  - Only systems fully respecting the conditions of the technical term “redundant”, meaning the system has no single point of failure, (including no master-slave relationships or common parallel electronic and de-centralized bypass) with proven installations.

  - Only systems with distributed bypass and redundant communication bus between units are accepted.

# Communication

In a standard version the UPS shall be equipped with:

  - Customer interface card with 9 x signalling voltage free contacts (4 programmable by user)

  - SNMP Card for remote Web monitoring (TCP/IP Network)

# Maintenance

  - The tenderer shall be responsible for the maintenance of the system after expiry of the warranty period. In the tender submission, the tenderer shall include a maintenance agreement for the subsequent maintenance of the system for consideration by the end-user.

  - The tenderer shall submit a checklist on the activities to be carried out for the system regular maintenance.

  - The tenderer shall provide evidence and undertake that round the clock on-call service is available to attend to system failure.

# Testing and commissioning

  - The UPS shall be tested at manufacturing side.

  - The UPS commissioning shall be executed by qualified service engineers, which perform the UPS pre-commissioning check, the parameters calibrations according to installation requirements and the start-up.

# Options

If required, the tendered shall be able to supply the following options, as integration of the UPS in a matching cabinet solution:

  - Input isolation transformer for galvanic separation of UPS from mains/utility supply to improve noise immunity but primarily as a safety device to prevent back-feed of DC voltage onto the mains.

  - Input/output voltage adaptation transformer to adapt UPS to non-standard voltage.

  - Maintenance Bypass Panel with 2 circuit breakers or 3 circuit breakers scheme to allow isolation of the UPS from the system.

  - Output Distribution Panel for multiple outlet connection

# Options for communications and monitoring

  - Remote Monitoring Solution allows remote monitoring and diagnostic of UPS of different capacity, different configurations and at different locations by different communication technologies (SNMP, GPRS).

The system shall also allow the manufacturer or its nearest regional service centre to gain access to the UPS installed at the user's premises for remote on-line diagnostic.

  - UPS Data Protection Software - The UPS have available data protection software compatible with Windows2000/NT/XP, UNIX, Novell, OS/2 and other common operating systems. The software shall be able to protect several hundred servers connected to one UPS system.

  - BMS support (Building Management System) - The UPS shall able to communicate over Modbus with a BMS system and provide the detailed values for every individual UPS in a parallel system.

UPS technical data

| Item | Description | Required |  | Offer |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | General |  |  |  |  |  |
| 1.1 | Manufacturer name and location |  |  |  |  |  |
| 1.2 | UPS model / type |  |  |  |  |  |
| 1.3 | UPS topology according to IEC62040-3 | VFI - SS - 111 |  |  |  |  |
|  | UPS power rating | 15-90 | kW |  |  |  |
| 1.4 | Module rating | 15 | kW |  | kW |  |
| 1.5 | Dimensions (WxDxH) |  | mm |  | mm |  |
| 1.6 | Weight |  |  |  |  |  |
| 1.7 | Protection degrees (IEC 60529) | IP20 |  |  |  |  |
| 1.8 | Color | RAL 9005 |  | RAL …… |  |  |
| 1.9 | Continuous operating temperature | 0 – 40 | °C |  | °C |  |
| 1.10 | Operating relative temperature | up to 95 | % |  | % |  |
| 1.11 | Cable entry | Top and Bottom |  |  |  |  |
| 1.12 | System efficiency | 93.0 | % |  | % |  |
| 1.15 | Efficiency at 100% load (ECO mode) | 98% | % |  | % |  |
| 1.16 | Installation | 500mm rear free space |  |  |  |  |
| 1.17 | Normal UPS operation | front access |  |  |  |  |
| 1.18 | Internal static bypass | Centralized |  |  |  |  |
| 1.19 | Applicable standard – safety | UL 1778 5th / CSA C22.2 No. 107.3 |  |  |  |  |
| 1.20 | Applicable standard – EMC | FCC part 15 class A |  |  |  |  |
| 2 | Parallel operation |  |  |  |  |  |
| 2.1 | Parallel operation for redundancy or capacity | up to 3 units in parallel (270kW) |  |  |  |  |
| 2.2 | UPS parallel bypass | Decentralized |  |  |  |  |
| 2.3 | Current share between units | +/-5 | % |  | % |  |
| 2.4 | Common Battery Configuration | Up to 3 UPS |  |  |  |  |

- UPS technical data

| Item | Description | Required |  | Offer |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 3 | UPS input characteristics |  |  |  |  |  |
| 3.1 | Input voltage | 3x208 + N | V |  | V |  |
| 3.2 | Input voltage range | 166-261 | V |  | V |  |
| 3.3 | Input frequency | 60 | Hz |  | Hz |  |
| 3.4 | UPS input current harmonic distortion | <4% at 100% load | % |  |  |  |
| 3.5 | Input power factor | 0.99 |  |  |  |  |
| 4 | UPS output characteristics |  |  |  |  |  |
| 4.2 | UPS output nominal power | 90 | kVA |  | kVA |  |
| 4.3 | UPS output active power at pf=1 | 90 | kW |  | kW |  |
| 4.4 | Output voltage | 3 x 208 + N | V |  | V |  |
| 4.5 | Output frequency | 60 | Hz |  | Hz |  |
| 4.6 | Output voltage distortion THD100% linear load | <1.5 | % |  | % |  |
| 4.7 | Output voltage distortion THD 100% non-linear load (EN/IEC62040) | < 6 | % |  | % |  |
| 4.8 | Overload capability | 110% 60 min 125% 10 min 150% 1 min >150% 200ms |  |  |  |  |
| 4.9 | Short circuit characteristics | 3*In for 200 ms |  |  |  |  |
| 5 | UPS static bypass switch |  |  |  |  |  |
| 5.1 | Bypass input mains | Separated/common with rectifier |  |  |  |  |
| 5.2 | Voltage limits for inverter/bypass load transfer | + 10 | % |  |  |  |
| 5.3 | Overload capability | 110% continuous 130% 10 min 150% 1 min >150% 200ms |  |  |  |  |
| 5.4 | Electromechanic contactor for back-fed protection integrated in UPS cabinet | Yes |  |  |  |  |
| 5.5 | Design | Centralized among internal power modules |  |  |  |  |

UPS technical data

| Item | Description | Required |  | Offer |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | Battery |  |  |  |  |  |
| 6.1 | Battery type |  |  |  |  |  |
| 6.2 | Battery model / type |  |  |  |  |  |
| 6.3 | Autonomy at 100% load |  | min |  | min |  |
| 6.4 | Floating voltage | 545 | V dc |  | V dc |  |
| 6.5 | Boost charging voltage |  | V dc |  | V dc |  |
| 6.6 | Number of battery blocks (12V) | 40 |  |  |  |  |
| 6.7 | Design | Common battery among power modules |  |  |  |  |
| 6.8 | Battery cabinet/rack dimensions WxDxH |  | mm |  | mm |  |
| 6.9 | Charging current | 9 Amps/module | A |  | A |  |
| 7 | UPS interfacing |  |  |  |  |  |
| 7.1 | Voltage free contacts | 9 |  |  |  |  |
| 7.2 | SNMP Card |  |  |  |  |  |
| 8 | Options |  |  |  |  |  |
| 8.1 | Input isolation transformer |  |  |  |  |  |
| 8.2 | Voltage Adaptation Transformers |  |  |  |  |  |
| 8.3 | Maintenance Bypass Panel |  |  |  |  |  |
| 8.3 | Output Distribution Panel |  |  |  |  |  |