## CSL3 K1
TYPICAL TRANSFORMER PERFORMANCE DATA
Copper 480V DELTA TO 208/120V WYE
Ultra High Energy Efficient TRANSFORMERS
| KVA | K FACTOR | oC RISE | CAT NO | LOSSES IN WATTS |  |  | EFFICIENCY | [5 empty] | % REGULATION |  | %R | %X | % Z |  |  | X/R | DIMENSIONS |  |  | WT. LBS. | dB | Ins | Frame | Outline
[5 empty] | No Load | Load | Total | .16L | .25L | .35L | .50L | .75L | FULL | 1.0 PF | .8 PF | [6 empty] | HT | W | D |  |  | Sys
| 15 |  | 150 | 9T73C9871 | 49 | 707 | 756 |  | 97.8 | 98.8 | 97.5 | 96.79 | 96 | 5.2 | 5.4 | 5.4 | 2.2 | 5.7 | 90 | 10kA | 0.40741 | 27.3 | 18.7 | 16.9 | 240 | 45 | 220C | ST371
|  | K1 | 115 | 9T73C9871G13 | 75 | 321 | 396 |  | 97.6 | 98 | 98.1 | 98 | 97.7 | 2.4 | 2.6 | 2.4 | 1.2 | 2.6 |  |  | 0.5 | 27.3 | 18.7 | 16.9 | 240 | 45 | 220C | ST371
|  |  | 80 | 9T73C9871G80 |  |  | 0 | [13 empty] | #DIV/0! | [8 empty] | 2.4% Z. Worst case secondary
| 30 |  | 150 | 9T73C9872 | 85 | 1023 | 1108 |  | 98.2 | 98.3 | 98.1 | 97.6 | 97 | 3.8 | 4.7 | 3.9 | 3.1 | 4.8 |  |  | 0.79487 | 32.1 | 23.8 | 18.4 | 360 | 45 | 220C | ST372
|  | K1 | 115 | 9T73C9872G13 | 63 | 1077 | 1140 |  | 98.4 | 98.3 | 98.1 | 97.4 | 96.8 | 3.8 | 5.2 | 3.9 | 4 | 5.6 |  |  | 1.0256 | 32.1 | 23.8 | 18.4 | 360 | 45 | 220C | ST372
|  |  | 80 | 9T73C9872G80 |  |  | 0 | [13 empty] | #DIV/0!
| 45 |  | 150 | 9T73C9873 | 97 | 1417 | 1514 |  | 98.5 | 98.5 | 98.3 | 97.8 | 97.3 | 3.5 | 4.5 | 3.6 | 3.1 | 5 |  |  | 0.86111 | 32.2 | 23.8 | 18.4 | 460 | 45 | 220C | ST373
|  | K1 | 115 | 9T73C9873G13 | 88 | 1408 | 1496 |  | 98.5 | 98.5 | 98.3 | 97.7 | 97.2 | 3.5 | 4.9 | 3.5 | 3.9 | 5.1 |  |  | 1.1143 | 32.2 | 23.8 | 18.4 | 460 | 45 | 220C | ST373
|  |  | 80 | 9T73C9873G80 |  |  | 0 | [13 empty] | #DIV/0!
| 75 |  | 150 | 9T73C9874 | 143 | 2147 | 2290 |  | 98.7 | 98.7 | 98.5 | 98 | 97.5 | 3.2 | 4.4 | 3.3 | 3.2 | 4.9 |  |  | 0.9697 | 35.7 | 31.8 | 24 | 690 | 50 | 220C | ST374
|  | K1 | 115 | 9T73C9874G13 | 149 | 1639 | 1788 |  | 98.7 | 98.7 | 98.6 | 98.3 | 97.9 | 2.4 | 4 | 2.4 | 3.8 | 4.6 |  |  | 1.5833 | 35.7 | 31.8 | 24 | 690 | 50 | 220C | ST374
|  |  | 80 | 9T73C9874G80 |  |  | 0 | [13 empty] | #DIV/0!
| 112.5 |  | 150 | 9T73C9875 | 200 | 2883 | 3083 |  | 98.8 | 98.8 | 98.6 | 98.2 | 97.8 | 2.7 | 4.5 | 2.7 | 4.3 | 5.1 |  |  | 1.5926 | 39.9 | 31.8 | 24 | 850 | 50 | 220C | ST375
|  | K1 | 115 | 9T73C9875G15 |  |  | 0 | [13 empty] | #DIV/0!
|  |  | 80 | 9T73C9875G80 |  |  | 0 | [13 empty] | #DIV/0!
| 150 |  | 150 | 9T73C9876 | 203 | 3882 | 4085 |  | 98.9 | 98.9 | 98.7 | 98.3 | 97.8 | 3 | 4.8 | 3 | 4.4 | 5.4 |  |  | 1.4667 | 45.9 | 34.8 | 24 | 1190 | 50 | 220C | ST376
|  | K1 | 115 | 9T73C9876G15 |  |  | 0 | [13 empty] | #DIV/0!
|  |  | 80 | 9T73C9876G80 |  |  | 0 | [13 empty] | #DIV/0!
| 225 |  | 150 | 9T73C9877 | 313 | 3890 | 4203 |  | 99.1 | 99.1 | 99 | 98.8 | 98.5 | 1.9 | 3.9 | 1.9 | 4.1 | 4.6 |  |  | 2.1579 | 45.5 | 38.5 | 33 | 1710 | 55 | 220C | ST377
|  | K1 | 115 | 9T73C9877G15 |  |  | 0 | [13 empty] | #DIV/0!
|  |  | 80 | 9T73C9877G80 |  |  | 0 | [13 empty] | #DIV/0!
| 300 |  | 150 | 9T73C9878 | 330 | 7444 | 7774 |  | 99.1 | 99 | 98.8 | 98.4 | 97.9 | 2.5 | 5.4 | 2.3 | 6.3 | 6.7 |  |  | 2.7391 | 57.1 | 38.5 | 33 | 3170 | 55 | 220C | ST378
|  | K1 | 115 | 9T73C9878G15 |  |  | 0 | [13 empty] | #DIV/0!
|  |  | 80 | 9T73C9878G80 |  |  | 0 | [13 empty] | #DIV/0!
*

## CSL3 K4
TYPICAL TRANSFORMER PERFORMANCE DATA
Copper 480V DELTA TO 208/120V WYE
Ultra High Energy Efficient TRANSFORMERS
KVA | K FACTOR | oC RISE | CAT NO | LOSSES IN WATTS |  |  | EFFICIENCY | [5 empty] | % REGULATION |  | %R | %X | % Z |  | X/R | DIMENSIONS |  |  | WT. LBS. | dB | Ins |  |  |  | SECONDARY
|  |  |  | No Load | Load | Total | .16L | .25L | .35L | .50L | .75L | FULL | 1.0 PF | .8 PF | [5 empty] | HT | W | D |  |  | Sys | Frame | Outline |  | S C AMPS
15 | 4 | 150 | 9T73C9461G03 | 76 | 308 | 384 | 96.8 | 97.6 | 98 | 98.2 | 98.1 | 97.9 | 2.5 | 3.2 | 2.4 | 1.9 | 3.1 |  | 0.79167 | 32.1 | 23.8 | 18.4 | 360 | 45 | 220C | ST372 |  |  | 1344.086
|  | 115 | 9T73C9461G13 | 76 | 292 | 368 | 96.8 | 97.6 | 98 | 98.2 | 98.1 | 97.9 | 2.3 | 3 | 2.2 | 1.9 | 3 |  | 0.86364 | 32.1 | 23.8 | 18.4 | 360 | 45 | 220C | ST372 |  |  | 1388.8889
|  | 80 | 9T73C9461G83 |  |  | 0 | [21 empty] | 2.4% Z. Worst case secondary | #DIV/0!
30 | 4 | 150 | 9T73C9462G03 |  |  | 0 |  | 98.33 | 98.47 | 98.4 | 98.13 | 97.75 | 2.75 | 3.66 | 2.82 | 2.55 | 3.8 | 10kA | 0.90426 | [9 empty] | 2192.9825
|  | 115 | 9T73C9462G13 | 90 | 695 | 785 | 96.7 | 98.3 | 98.5 | 98.4 | 98.1 | 97.7 | 2.7 | 3.8 | 2.6 | 2.6 | 3.6 | 10kA | 1 | 32.2 | 23.8 | 18.4 | 460 | 45 | 220C | ST373 |  |  | 2314.8148
|  | 80 | 9T73C9462G83 |  |  | 0 | [22 empty] | #DIV/0!
45 | 4 | 150 | 9T73C9463G03 | 133 | 843 | 976 | 98 | 98.63 | 98.76 | 98.75 | 98.54 | 98.25 | 2.3 | 3.4 | 2.16 | 2.54 | 3.33 | 10kA | 1.1759 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  |  | 3753.7538
|  | 115 | 9T73C9463G13 | 133 | 780 | 913 | 98 | 98.63 | 98.76 | 98.74 | 98.53 | 98.23 | 2.1 | 3.2 | 1.97 | 2.54 | 3.22 | 10kA | 1.2893 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  |  | 3881.9876
|  | 80 | 9T73C9463G83 | 133 | 751 | 884 | 98 | 98.62 | 98.75 | 98.73 | 98.52 | 98.22 | 1.9 | 3 | 1.8 | 2.5 | 3.1 | 10kA | 1.3889 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  |  | 4032.2581
75 | 4 | 150 | 9T73C9464G03 | 185 | 1196 | 1381 | 98.6 | 98.7 | 98.85 | 98.87 | 98.7 | 98.47 | 2 | 3.4 | 1.87 | 2.9 | 3.45 | 10kA | 1.5508 | 39.9 | 31.8 | 24 | 850 | 50 | 220C | ST375 |  |  | 6038.6473
|  | 115 | 9T73C9464G13 | 185 | 1134 | 1319 | 98.6 | 98.7 | 98.85 | 98.86 | 98.7 | 98.46 | 1.8 | 3.2 | 1.68 | 2.9 | 3.35 | 10kA | 1.7262 | 39.9 | 31.8 | 24 | 850 | 50 | 220C | ST375 |  |  | 6218.9055
|  | 80 | 9T73C9464G83 |  |  | 0 |  | 98.49 | 98.7 | 98.78 | 98.68 | 98.48 | 1.41 | 2.44 | 1.42 | 2.33 | 2.7 | 10kA | 1.6408 | [9 empty] | 7716.0494
112.5 | 4 | 150 | 9T73C9465G03 |  |  | 0 |  | 98.75 | 98.79 | 98.7 | 98.39 | 98.01 | 2.59 | 4.02 | 2.57 | 3.5 | 4.3 | 10kA | 1.3619 | [9 empty] | 7267.4419
|  | 115 | 9T73C9465G13 | 229 | 2378 | 2607 | 98.5 | 98.74 | 98.8 | 98.7 | 98.4 | 98 | 2.5 | 4.2 | 2.4 | 3.5 | 4.2 | 10kA | 1.4583 | 45.9 | 34.8 | 24 | 1190 | 50 | 220C | ST376 |  |  | 7440.4762
|  | 80 | 9T73C9465G83 | 301 | 1257 | 1558 | 98.2 | 98.69 | 98.88 | 98.95 | 98.87 | 98.7 | 1.4 | 2.7 | 1.3 | 2.58 | 2.8 | 10kA | 1.9846 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377 |  |  | 11160.7143
150 | 4 | 150 | 9T73C9466G03 | 301 | 2521 | 2822 | 98.2 | 98.87 | 98.96 | 98.92 | 98.72 | 98.45 | 2.1 | 3.8 | 1.98 | 3.4 | 4 | 10kA | 1.7172 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377 |  |  | 10416.6667
|  | 115 | 9T73C9466G13 | 301 | 2390 | 2691 | 98.6 | 98.86 | 98.95 | 98.92 | 98.71 | 98.44 | 1.9 | 3.6 | 1.77 | 3.44 | 3.9 | 10kA | 1.9435 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377
|  | 80 | 9T73C9466G83 | [25 empty] | #DIV/0!
225 | 4 | [27 empty] | #DIV/0!
#DIV/0!
300 | 4 | [27 empty] | #DIV/0!
#DIV/0!
#DIV/0!
|  |  | = | checked

## CSL3 K13
TYPICAL TRANSFORMER PERFORMANCE DATA
Copper 480V DELTA TO 208/120V WYE
Ultra High Energy Efficient TRANSFORMERS
KVA | K FACTOR | oC RISE | CAT NO | LOSSES IN WATTS |  |  | EFFICIENCY | [5 empty] | % REGULATION |  | %R | %X | % Z |  | X/R | DIMENSIONS |  |  | WT. LBS. | dB | Ins |  |  | SECONDARY
|  |  |  | No Load | Load | Total | .16L | .25L | .35L | .50L | .75L | FULL | 1.0 PF | .8 PF | [5 empty] | HT | W | D |  |  | Sys | Frame | Outline | S C AMPS
15 | 13 | 150 | 9T73C9471G03 | [24 empty] | #DIV/0!
|  | 115 | 9T73C9471G13 | 76 | 292 | 368 | 96.8 | 97.6 | 98 | 98.2 | 98.1 | 97.9 | 2.3 | 3 | 2.2 | 1.9 | 3 |  | 0.86364 | 32.1 | 23.8 | 18.4 | 360 | 45 | 220C | ST372
|  | 80 | 9T73C9471G83 |  |  | 0 | [12 empty] | #DIV/0! | [8 empty] | #DIV/0!
30 | 13 | 150 | 9T73C9472G03 | 90 | 733 | 823 | 97.9 | 98.3 | 98.5 | 98.4 | 98.1 | 97.7 | 2.8 | 3.7 | 2.8 | 2.6 | 3.8 | 10kA | 0.92857 | 32.2 | 23.8 | 18.4 | 460 | 45 | 220C | ST373 |  | 2192.9825
|  | 115 | 9T73C9472G13 | 90 | 695 | 785 | 97.9 | 98.3 | 98.5 | 98.4 | 98.1 | 97.7 | 2.7 | 3.8 | 2.6 | 2.6 | 3.6 | 10kA | 1 | 32.2 | 23.8 | 18.4 | 460 | 45 | 220C | ST373
|  | 80 | 9T73C9472G83 |  |  | 0 | [12 empty] | #DIV/0! | [8 empty] | 2314.8148
45 | 13 | 150 | 9T73C9473G03 | 133 | 843 | 976 | 98 | 98.6 | 98.8 | 98.8 | 98.5 | 98.3 | 2.11 | 3.2 | 2 | 2.5 | 3.3 | 10kA | 1.25 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  | 3787.8788
|  | 115 | 9T73C9473G13 | 133 | 780 | 913 | 98 | 98.6 | 98.8 | 98.7 | 98.5 | 98.2 | 2.1 | 3.2 | 2 | 2.5 | 3.2 | 10kA | 1.25 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  | 3906.25
|  | 80 | 9T73C9473G83 | 133 | 751 | 884 | 98 | 98.6 | 98.8 | 98.7 | 98.5 | 98.2 | 1.9 | 3 | 1.8 | 2.5 | 3.1 | 10kA | 1.3889 | 35.7 | 31.8 | 24 | 690 | 45 | 220C | ST374 |  | 4032.2581
75 | 13 | 150 | 9T73C9474G03 | 185 | 1196 | 1381 | 98.3 | 98.7 | 98.9 | 98.9 | 98.7 | 98.5 | 2 | 3.4 | 1.9 | 2.9 | 3.5 | 10kA | 1.5263 | 39.9 | 31.8 | 24 | 850 | 50 | 220C | ST375 |  | 5952.381
|  | 115 | 9T73C9474G13 | 185 | 1133 | 1318 | 98.4 | 98.7 | 98.9 | 98.9 | 98.7 | 98.5 | 1.8 | 3.2 | 1.7 | 2.9 | 3.4 | 10kA | 1.7059 | 39.9 | 31.8 | 24 | 850 | 50 | 220C | ST375
|  | 80 | 9T73C9474G83 |  |  | 0 | [12 empty] | #DIV/0! | [8 empty] | 6127.451
112.5 | 13 | 150 | 9T73C9475G03 |  |  | 0 | [11 empty] | 10kA | #DIV/0! | [8 empty] | #DIV/0!
|  | 115 | 9T73C9475G13 | 301 | 1340 | 1641 | 98.2 | 98.7 | 98.9 | 99 | 98.9 | 98.7 | 1.4 | 2.7 | 1.3 | 2.6 | 2.9 | 10kA | 2 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377 |  | 10775.8621
|  | 80 | 9T73C9475G83 | 301 | 1257 | 1558 | 98.2 | 98.7 | 98.9 | 99 | 98.9 | 98.7 | 1.2 | 2.7 | 1.3 | 2.6 | 2.8 | 10kA | 2 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377 |  | 11160.7143
150 | 13 | 150 | 9T73C9476G03 | 301 | 2521 | 2822 | 98.6 | 98.9 | 99 | 98.9 | 98.7 | 98.5 | 2.1 | 3.8 | 2 | 3.4 | 3.9 | 10kA | 1.7 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377 |  | 10683.7607
|  | 115 | 9T73C9476G13 | 301 | 2390 | 2691 | 98.5 | 98.9 | 99 | 98.9 | 98.7 | 98.4 | 1.9 | 3.6 | 1.8 | 3.4 | 3.9 | 10kA | 1.8889 | 45.5 | 38.5 | 33 | 1710 | 50 | 220C | ST377
|  | 80 | 9T73C9476G83 |  |  | 0 | [12 empty] | #DIV/0!
225 | [27 empty] | #DIV/0!
#DIV/0!
300 | [27 empty] | #DIV/0!
#DIV/0!
#DIV/0!
|  |  |  | = | checked

## Harm Mit 0 Deg
TYPICAL TRANSFORMER PERFORMANCE DATA
Copper 480V DELTA TO 208/120V WYE
Ultra High Energy Efficient TRANSFORMERS
HARMONIC MITIGATING 0 DEGREE PHASE SHIFT
KVA | K FACTOR | oC RISE | CAT NO | LOSSES IN WATTS |  |  | EFFICIENCY | [5 empty] | % REGULATION |  | %R | %X | % Z | X/R | DIMENSIONS |  |  | WT. LBS. | dB | Ins
|  |  |  | No Load | Load | Total | .16L | .25L | .35L | .50L | .75L | FULL | 1.0 PF | .8 PF |  |  |  |  | HT | W | D |  |  | Sys | Frame | Outline
15 |  | 150 | 9T76H9871G03
115
80
30 |  | 150 | 9T76H9872G03
115
80
45 |  | 150 | 9T76H9873G03
115
80
75 |  | 150 | 9T76H9874G03
115
80
112.5 |  | 150 | 9T76H9875G03
115
80
150 |  | 150 | 9T76H9876G03
115
80
225 |  | 150 | 9T76H9877G03
115
80
300 |  | 150 | 9T76H9878G03
115
80

## Harm Mit 30 Deg
TYPICAL TRANSFORMER PERFORMANCE DATA
Copper 480V DELTA TO 208/120V WYE
Ultra High Energy Efficient TRANSFORMERS
HARMONIC MITIGATING -30 DEGREE PHASE SHIFT
KVA | K FACTOR | oC RISE | CAT NO | LOSSES IN WATTS |  |  | EFFICIENCY | [5 empty] | % REGULATION |  | %R | %X | % Z | X/R | DIMENSIONS |  |  | WT. LBS. | dB | Ins
|  |  |  | No Load | Load | Total | .16L | .25L | .35L | .50L | .75L | FULL | 1.0 PF | .8 PF |  |  |  |  | HT | W | D |  |  | Sys | Frame | Outline
15 |  | 150 | 9T77H9871G03
115
80
30 |  | 150 | 9T77H9872G03
115
80
45 |  | 150 | 9T77H9873G03
115
80
75 |  | 150 | 9T77H9874G03
115
80
112.5 |  | 150 | 9T77H9875G03
115
80
150 |  | 150 | 9T77H9876G03
115
80
225 |  | 150 | 9T77H9877G03
115
80
300 |  | 150 | 9T77H9878G03
115
80